## Important information
Solar PV Assessment Tool for the Australian Chicken Meat Industry
Version: 1 (July 2014)
Purpose
The purpose of this calculator is to provide meat chicken farmers with an indication as to whether installing a solar photovoltaic (PV) system is likely to be financially viable for their farm. The calculator is a first pass assessment tool and should only be used as the first step in assessing the feasibility of solar PV system. The calculator has been developed specifically for the Australian Chicken Meat Industry.
Assumptions and limitations
The results shown in this calculator are based on assumptions made by GHD as outlined below. GHD disclaims liability arising from any of the assumptions being incorrect. The calculations are based on the following assumptions and limitations: - Efficiency of solar PV modules is 15% - Solar PV system efficiency is 80% - Solar PV system degradation is 0.5% per annum - System life is 25 years with an inverter replacement after 15 years - No upgrades are required to existing electrical infrastructure - Solar PV systems are roof mounted and structural upgrades to the chicken sheds are not required - Default system cost is based on average costs for a 10 kW system and includes discounts for Small-scale Technology Certificates (STCs) - [1] - Maximum system size is 100 kW - Electricity costs increase at 2.5% per annum - Operational costs are 1% of the system costs and increase at 3% per annum - Revenue from feed in tariffs is not considered - Where electricity tariffs are split into peak, off-peak, and shoulder tariffs: shoulder tariffs are assumed to apply from 6am to 3pm weekdays, and 6am to 6pm on weekends; peak tariffs are assumed to apply from 3pm to 6pm on weekdays. - 100% of the capital costs are borrowed - Solar generation is based on monthly data for solar radiation for each postcode in Australia (excluding external territories) - Solar generation is split between peak generation (Monday to Friday) and off-peak generation (Saturday and Sunday) - Solar generation may be higher than the estimates used in this model
Disclaimer
This calculator has been prepared by GHD for RIRDC and may only be used and relied on by RIRDC for the purpose outlined above. GHD otherwise disclaims responsibility to any person other than RIRDC arising in connection with this calculator. GHD also excludes implied warranties and conditions, to the extent legally permissible. This Document has been prepared subject to your acknowledgement that GHD is not qualified and/or accredited to give advice in relation to financial issues, legal issues, contractual issues, accounting issues, currency issues, tax issues, or to make financial forecasts that would require any of these areas of expertise. As such, nothing in this Document shall amount to advice in relation to these areas of expertise, or any other area of expertise. GHD recommends that users undertake their own comprehensive due diligence, risk assessment, and financial modelling processes, including seeking the advice of a qualified Financial Advisor.
References
[1] - http://www.solarchoice.net.au/blog/solar-pv-system-prices-australia-march-2014-100314/

## Instructions
Instructions
Step | Instructions | Further guidance
General | The 'Solar Assessment' contains blue shaded boxes to input data for the assessment. Results are displayed in the same worksheet. Some of the default values used in the calculations can be overridden with site specific or user specific assumptions.
1 - Property details | The following details are required for the assessment: - Postcode for the property - Solar PV system size in kW | Users can define the size of PV system they wish to consider. Assume a 5 kW system as default size. Feasibility of systems larger than 5 kW will need to consider the site's load profile, and should be discussed with your supplier.
2 - Electricity tariffs | Electricity tariffs from your latest electricity bill are required. The peak, off peak, and shoulder electricity tariffs should be easily located on your electricity bill. For all the other charges on you electricity bill (e.g. market, other network charges, environmental charges) add up all charges that have units of c/kWh and insert this value in the cell for "Total all other consumption based charges". Where electricity is charged at a flat rate regardless of time of use, this value should be allocated as both the peak and off-peak electricity rate. | Refer to the Guidelines for more information on the structure of your electricity bill.
3 - Electricity consumption | Peak and off peak electricity consumption for your previous twelve months are required. Insert the kWh of electricity consumed from your previous bills. | If you receive quarterly bills, divide the peak and off peak consumption by three and use this value for the respective months in the quarter.
4 - Results | Based on the information provided in Steps 1, 2 and 3 and the assumptions outlined in the 'Important information' worksheet, the feasibility of solar PV will be assessed as unlikely, marginal or likely. The classification is based on the internal rate of return (IRR) over the life of the system. A negative IRR is classified as "unlikely", an IRR between 0-10% is classified as "marginal" and an IRR greater than 10% is classified as "likely". A plot is provided of monthly electricity consumption (columns) and the predicted solar generation (line) to allow comparison of an appropriate system size.
5 - Adjusting default values | The default values for a number of parameters can be overridden. These parameters include: - The system cost - The interest rate for the borrowed capital costs - The discount factor used in the financial assessment calculations

## Solar assessment
Property details |  |  | Assumptions |  |  | Notes
|  |  | Parameter | Default | User Input
Property name/details |  | Optional | Unit cost of system ($/kW) - [1] | 1650 |  | This calculator provides a preliminary indication of whether a PV system is likely to be viable at a small scale (5 kW system size). For systems larger than 5 kW, the calculator provides an indication of the cost and electricity generation associated with such systems, but does not consider whether the solar generation is well suited to the site's electrical load. The viability of systems larger than 5 kW should be assessed by a suitably experienced professional.
Postcode |  | Required | Interest Rate for borrowing (%/year) | 5.25%
System size (kW) | 5 | Assume 5 kW as default 100 kW maximum | Discount Rate - [2] | 5.25%
|  |  | Estimated IRR value for calculations | 10%
Where a site's location and electricity prices indicate that solar PV might be feasible, meat chicken growers should then consider the following factors as a minimum in their feasibility assessment: the specific electrical load profile of their business and it's compatibility with solar generation; the terms of their electricity supply contracts - particularly any minimum consumption requirements; and the compatibility of site electrical infrastructure with a solar PV system. For more information refer to the RIRDC Solar guidelines for Australian meat chicken growers.
Tariff details from your latest electricity bill |  |  | Electricity consumption
Energy Charges |  |  | Month | Peak consumption (kWh) | Off peak consumption (kWh)
Peak energy (c/kWh) | 5 |  | January | 22000 | 22000
Off peak energy (c/kWh) | 3 |  | February | 16000 | 16000
Shoulder energy (c/kWh) |  | leave blank if not applicable | March | 22000 | 22000
Network Charges |  |  | April | 16000 | 16000
Peak energy (c/kWh) | 5 |  | May | 22000 | 22000 | This calculation tool only focusses on solar PV systems connected "behind the meter" to offset electricity usage
Off peak energy (c/kWh) | 1 |  | June | 16000 | 16000
Shoulder energy (c/kWh) |  | leave blank if not applicable | July | 22000 | 22000 | It is assumed that all electricity generated is consumed on site.
All Other Charges |  |  | August | 16000 | 16000 | Revenue from feed in tariffs is not considered
Total all other consumption based charges (c/kWh) | 5 | leave blank if not applicable | September | 22000 | 22000 | [1] - The unit cost of a system is the total cost of the system, divided by the system size (in kW), to give a system cost per kilowatt. For example, a 5kW system costing $8,250 has a unit cost of $1,650/kW. - Alternative system costs can be found on the Solar Choice website: http://www.solarchoice.net.au/
|  |  | October | 16000 | 16000
|  |  | November | 22000 | 22000
|  |  | December | 16000 | 16000
Results | [5 empty] | [2] - The discount rate is an interest rate used to bring future values into the present when considering the time value of money. The time value of money relates to the intuitive concept that $1 given to you today is worth more to you than a dollar given to you in a years' time. This is driven by two main factors: firstly, if you control the money today you can put it to work for you - earning interest or appreciating in value. Secondly, inflation decreases the purchasing value of money over time - meaning it takes more money to buy something in the future than to buy the same thing today. The discount rate is required to calculate discounted cashflow over time, and can be adjusted to suit personal requirements. (http://wiki.fool.com/Discount_rate)
Indicative Internal Rate of Return (Real) - [3] |  | No Result
Is solar PV feasible? |  | Unlikely
Estimated PV system cost |  | 8250
Estimated annual electricity generated (kWh) |  | #N/A
Proportion of electricity consumption offset by solar |  | #N/A
Shade free North facing roof area required (m2) |  | 32 |  |  |  | [3] - The Internal Rate of Return calculated here is indicative only, and is suitable only for determining the likelihood of a solar PV system being commercially viable, categorised as "Unlikely", "Marginal", or "Likely". It should not be relied upon as a representation of the likely internal rate of return that a customer should expect.

## Business case (hidden)
Month | Peak generation (kWh) | Off peak generation (kWh) | Original peak consumption (kWh) | Original off peak consumption (kWh) | Peak self consumption (kWh) | Off peak self consumption (kWh) | Exported to grid (kWh) | Peak imported from grid | Off peak imported from grid | Total solar PV generation | Total original consumption (kWh)
January | #N/A | #N/A | 22000 | 22000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44000
February | #N/A | #N/A | 16000 | 16000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32000
March | #N/A | #N/A | 22000 | 22000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44000
April | #N/A | #N/A | 16000 | 16000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32000
May | #N/A | #N/A | 22000 | 22000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44000
June | #N/A | #N/A | 16000 | 16000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32000
July | #N/A | #N/A | 22000 | 22000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44000
August | #N/A | #N/A | 16000 | 16000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32000
September | #N/A | #N/A | 22000 | 22000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44000
October | #N/A | #N/A | 16000 | 16000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32000
November | #N/A | #N/A | 22000 | 22000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44000
December | #N/A | #N/A | 16000 | 16000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32000
Total | #N/A | #N/A | 228000 | 228000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 456000 |  | #N/A
Year | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Electricity tariff
Total (Peak) (c/kWh) | 15 | 15.375 | 15.7594 | 16.1534 | 16.5572 | 16.9711 | 17.3954 | 17.8303 | 18.276 | 18.7329 | 19.2013 | 19.6813 | 20.1733 | 20.6777 | 21.1946 | 21.7245 | 22.2676 | 22.8243 | 23.3949 | 23.9798 | 24.5792 | 25.1937 | 25.8236 | 26.4692 | 27.1309 | 27.8092
Total (Off-peak) (c/kWh) | 9 | 9.225 | 9.4556 | 9.692 | 9.9343 | 10.1827 | 10.4372 | 10.6982 | 10.9656 | 11.2398 | 11.5208 | 11.8088 | 12.104 | 12.4066 | 12.7168 | 13.0347 | 13.3606 | 13.6946 | 14.0369 | 14.3879 | 14.7475 | 15.1162 | 15.4941 | 15.8815 | 16.2785 | 16.6855
Revenue
Value of Peak Electricity Consumed On-Site ($) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Value of Off-Peak Electricity Consumed On-Site ($) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Income from feed in tariff ($) | Row deleted
Tax payable ($) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Revenue ($) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Expenditure ($)
Indicative CAPEX ($) | -8250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indicative OPEX ($) | 0 | -82.5 | -84.975 | -87.5242 | -90.15 | -92.8545 | -95.6401 | -98.5093 | -101.4646 | -104.5085 | -107.6438 | -110.8731 | -114.1993 | -117.6253 | -121.154 | -124.7887 | -128.5323 | -132.3883 | -136.3599 | -140.4507 | -144.6642 | -149.0042 | -153.4743 | -158.0785 | -162.8209 | -167.7055
Total Annual Expenditure ($) | -8250 | -82.5 | -84.975 | -87.5242 | -90.15 | -92.8545 | -95.6401 | -98.5093 | -101.4646 | -104.5085 | -107.6438 | -110.8731 | -114.1993 | -117.6253 | -121.154 | -2624.7887 | -128.5323 | -132.3883 | -136.3599 | -140.4507 | -144.6642 | -149.0042 | -153.4743 | -158.0785 | -162.8209 | -167.7055
Finance
Interest Payment | 0 | -433.125 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Principal Payment | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Remaining Principal | -8250 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Net Results
Net after tax Nominal Value ($) | -8250 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Net after tax Real Value ($) | -8250 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cumulative Present Value ($) | -8250 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
IRR (Nominal) | #N/A
IRR (Real) | #N/A
NPV (Nominal) | #N/A
NPV (Real) | #N/A
Note on B20: Chris Davies: Returns values: If Shoulder Energy and Shoulder Network are blank, then (Peak Energy + Peak Network + Other charges). If either shoulder energy or shoulder network are greater than zero, it returns a value using 3/4 shoulder charges and 1/4 peak charges, reflecting the assumed 9/12 hours a day that shoulder charges will apply
Note on F1: Chris Davies: link to self consumption deleted
Note on G1: Chris Davies: link to InputSelfConsumption deleted

## Solar radiation for postcodes (hidden)
Postcode | January | February | March | April | May | June | July | August | September | October | November | December | Annual
800 | 19.5056 | 18.377 | 20.9905 | 22.3097 | 20.6688 | 19.9524 | 20.9676 | 23.0634 | 23.6808 | 23.6643 | 22.9519 | 20.236 | 21.364
810 | 19.4716 | 18.3872 | 21.3025 | 22.7548 | 20.9953 | 20.1532 | 21.3141 | 23.542 | 24.9677 | 24.7879 | 23.5614 | 20.3119 | 21.7958
812 | 19.4865 | 18.3958 | 20.8871 | 22.5653 | 20.8456 | 20.0099 | 21.105 | 23.2043 | 24.1211 | 23.9388 | 22.9415 | 20.1975 | 21.4749
820 | 19.5056 | 18.377 | 20.9905 | 22.3097 | 20.6688 | 19.9524 | 20.9676 | 23.0634 | 23.6808 | 23.6643 | 22.9519 | 20.236 | 21.364
822 | 20.5076 | 19.7922 | 22.221 | 22.8328 | 20.572 | 19.7932 | 20.8769 | 23.1271 | 24.8094 | 24.5923 | 24.3204 | 21.4653 | 22.0758
828 | 19.1727 | 18.091 | 20.9216 | 22.5722 | 20.8372 | 20.0692 | 21.0682 | 22.9892 | 23.926 | 23.4566 | 22.595 | 19.7909 | 21.2908
829 | 19.1559 | 18.0334 | 21.1632 | 22.7001 | 20.8109 | 20.0705 | 21.1021 | 22.9843 | 23.9736 | 23.4335 | 22.5513 | 19.9204 | 21.3249
830 | 19.3596 | 18.0921 | 21.2431 | 22.5783 | 20.9355 | 20.1584 | 21.2306 | 23.3017 | 24.5913 | 24.124 | 22.7744 | 20.1988 | 21.549
832 | 19.2253 | 18.0295 | 21.1962 | 22.7539 | 20.7972 | 20.0596 | 21.0522 | 22.7922 | 23.8222 | 22.9501 | 22.3865 | 19.9044 | 21.2474
835 | 19.1699 | 17.9904 | 21.3194 | 22.8014 | 20.7763 | 20.0061 | 21.039 | 22.8648 | 23.893 | 22.9923 | 22.3887 | 19.9856 | 21.2689
836 | 19.3271 | 18.2689 | 21.5527 | 22.9067 | 20.8876 | 20.0532 | 21.0803 | 22.824 | 23.8021 | 23.0026 | 22.6073 | 20.1515 | 21.372
837 | 19.1911 | 18.1504 | 21.3289 | 22.8666 | 20.815 | 19.98 | 20.9458 | 22.7828 | 23.7793 | 23.114 | 23.0008 | 20.1035 | 21.3382
838 | 19.1485 | 17.958 | 21.1977 | 22.7663 | 20.7865 | 19.9488 | 20.9196 | 22.6504 | 23.5815 | 23.0109 | 22.7513 | 20.0318 | 21.2293
840 | 19.0133 | 18.0196 | 20.8922 | 22.4674 | 20.6205 | 19.8975 | 20.936 | 22.5974 | 23.4839 | 22.66 | 22.4058 | 19.7363 | 21.0608
841 | 19.1976 | 18.1253 | 21.2248 | 22.6828 | 20.6071 | 19.9117 | 20.927 | 22.69 | 23.5834 | 23.0714 | 22.7421 | 20.1641 | 21.2439
845 | 19.8796 | 19.0089 | 21.8278 | 22.9857 | 20.7337 | 19.9924 | 20.9732 | 22.7772 | 23.6597 | 23.4431 | 23.5303 | 20.6991 | 21.6259
846 | 20.4757 | 19.3155 | 22.049 | 22.8142 | 20.6983 | 19.9156 | 20.8943 | 22.7072 | 23.8321 | 23.3335 | 23.313 | 21.2341 | 21.7152
847 | 21.4997 | 20.4608 | 22.4849 | 22.8211 | 20.5653 | 19.7475 | 20.7985 | 22.9753 | 24.1322 | 24.1081 | 24.6164 | 22.8043 | 22.2512
850 | 22.4333 | 21.6395 | 23.1217 | 22.7841 | 20.6578 | 19.668 | 20.5956 | 22.8068 | 24.4176 | 24.8128 | 24.9969 | 23.6551 | 22.6324
852 | 23.6921 | 22.6264 | 23.4177 | 22.5714 | 20.0352 | 18.7665 | 19.8385 | 22.4058 | 24.1529 | 24.8197 | 25.0451 | 24.123 | 22.6245
853 | 22.3825 | 21.7641 | 23.2094 | 22.9456 | 20.6557 | 19.6502 | 20.59 | 22.8465 | 24.3703 | 24.7114 | 25.0911 | 23.4467 | 22.6386
854 | 21.6348 | 20.3938 | 21.7825 | 21.8445 | 20.0294 | 18.8331 | 20.117 | 22.5834 | 24.85 | 25.2703 | 24.9466 | 22.9495 | 22.1029
860 | 26.1775 | 24.5281 | 24.053 | 22.2241 | 18.9105 | 17.3714 | 18.5756 | 21.5647 | 24.1342 | 25.1523 | 26.1339 | 26.2561 | 22.9234
862 | 24.9453 | 23.9783 | 23.8417 | 21.7081 | 19.219 | 17.8665 | 18.9872 | 21.7117 | 24.1809 | 25.5186 | 26.3298 | 25.3982 | 22.8071
870 | 27.7459 | 24.406 | 24.0314 | 20.6239 | 16.5393 | 14.9473 | 16.1992 | 19.4643 | 22.4159 | 24.6247 | 26.3557 | 26.4694 | 21.9853
872 | 27.5712 | 24.4163 | 23.749 | 20.6455 | 16.6541 | 15.1738 | 16.3027 | 19.6496 | 23.0072 | 25.2087 | 26.6109 | 26.1988 | 22.099
880 | 20.1874 | 18.3989 | 20.1809 | 19.9072 | 19.0467 | 17.9436 | 19.4329 | 22.4316 | 24.6777 | 25.7152 | 24.8443 | 21.4702 | 21.1864
885 | 21.6345 | 20.2201 | 20.6965 | 19.6183 | 18.9387 | 18.3227 | 19.9334 | 22.5469 | 24.6616 | 25.7719 | 25.0963 | 22.6462 | 21.6739
886 | 20.2951 | 19.5976 | 21.9894 | 22.7228 | 20.6795 | 19.9706 | 21.0201 | 23.2764 | 24.741 | 24.7539 | 24.3229 | 21.1513 | 22.0434
2000 | 23.3113 | 20.8006 | 17.326 | 14.0295 | 9.9068 | 8.975 | 9.8707 | 13.553 | 17.0242 | 19.9311 | 21.1642 | 23.3355 | 16.6023
2006 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2007 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2008 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2009 | 23.3113 | 20.8006 | 17.326 | 14.0295 | 9.9068 | 8.975 | 9.8707 | 13.553 | 17.0242 | 19.9311 | 21.1642 | 23.3355 | 16.6023
2010 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2011 | 23.3113 | 20.8006 | 17.326 | 14.0295 | 9.9068 | 8.975 | 9.8707 | 13.553 | 17.0242 | 19.9311 | 21.1642 | 23.3355 | 16.6023
2015 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2016 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2017 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2018 | 23.8005 | 21.37 | 17.7929 | 14.022 | 9.8479 | 8.9257 | 9.7963 | 13.4453 | 17.0384 | 20.1496 | 21.3014 | 23.8636 | 16.7795
2019 | 23.8005 | 21.37 | 17.7929 | 14.022 | 9.8479 | 8.9257 | 9.7963 | 13.4453 | 17.0384 | 20.1496 | 21.3014 | 23.8636 | 16.7795
2020 | 23.8005 | 21.37 | 17.7929 | 14.022 | 9.8479 | 8.9257 | 9.7963 | 13.4453 | 17.0384 | 20.1496 | 21.3014 | 23.8636 | 16.7795
2021 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2022 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2023 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2024 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2025 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2026 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2027 | 23.6162 | 21.1972 | 17.8055 | 14.3344 | 9.9242 | 8.8767 | 9.8037 | 13.5648 | 17.0928 | 20.2309 | 21.7098 | 23.5883 | 16.812
2028 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2029 | 23.6162 | 21.1972 | 17.8055 | 14.3344 | 9.9242 | 8.8767 | 9.8037 | 13.5648 | 17.0928 | 20.2309 | 21.7098 | 23.5883 | 16.812
2030 | 23.6162 | 21.1972 | 17.8055 | 14.3344 | 9.9242 | 8.8767 | 9.8037 | 13.5648 | 17.0928 | 20.2309 | 21.7098 | 23.5883 | 16.812
2031 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2032 | 24.1549 | 21.6773 | 18.1993 | 14.4785 | 9.8983 | 8.8369 | 9.7232 | 13.4689 | 17.1339 | 20.3379 | 21.6577 | 24.0304 | 16.9664
2033 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2034 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2035 | 24.1549 | 21.6773 | 18.1993 | 14.4785 | 9.8983 | 8.8369 | 9.7232 | 13.4689 | 17.1339 | 20.3379 | 21.6577 | 24.0304 | 16.9664
2036 | 24.1549 | 21.6773 | 18.1993 | 14.4785 | 9.8983 | 8.8369 | 9.7232 | 13.4689 | 17.1339 | 20.3379 | 21.6577 | 24.0304 | 16.9664
2037 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2038 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2039 | 23.0637 | 20.5479 | 17.1181 | 14.0026 | 9.9695 | 8.9974 | 9.9116 | 13.5101 | 16.8829 | 19.8155 | 20.988 | 23.216 | 16.5019
2040 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2041 | 23.3113 | 20.8006 | 17.326 | 14.0295 | 9.9068 | 8.975 | 9.8707 | 13.553 | 17.0242 | 19.9311 | 21.1642 | 23.3355 | 16.6023
2042 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2043 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2044 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2045 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2046 | 23.0637 | 20.5479 | 17.1181 | 14.0026 | 9.9695 | 8.9974 | 9.9116 | 13.5101 | 16.8829 | 19.8155 | 20.988 | 23.216 | 16.5019
2047 | 23.0637 | 20.5479 | 17.1181 | 14.0026 | 9.9695 | 8.9974 | 9.9116 | 13.5101 | 16.8829 | 19.8155 | 20.988 | 23.216 | 16.5019
2048 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2049 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2050 | 23.5408 | 20.9659 | 17.6193 | 14.0571 | 9.8764 | 8.8998 | 9.755 | 13.4522 | 17.0651 | 20.028 | 21.2493 | 23.5865 | 16.6746
2052 | 23.9009 | 21.268 | 18.04 | 14.4287 | 9.9417 | 8.872 | 9.7143 | 13.4669 | 17.182 | 20.2716 | 21.7065 | 23.9252 | 16.8931
2060 | 23.3113 | 20.8006 | 17.326 | 14.0295 | 9.9068 | 8.975 | 9.8707 | 13.553 | 17.0242 | 19.9311 | 21.1642 | 23.3355 | 16.6023
2061 | 23.3113 | 20.8006 | 17.326 | 14.0295 | 9.9068 | 8.975 | 9.8707 | 13.553 | 17.0242 | 19.9311 | 21.1642 | 23.3355 | 16.6023
2062 | 22.9909 | 20.6407 | 17.2102 | 13.9702 | 9.9444 | 9.0727 | 9.9464 | 13.5317 | 16.8751 | 19.8717 | 21.0668 | 23.1276 | 16.5207
2063 | 22.9909 | 20.6407 | 17.2102 | 13.9702 | 9.9444 | 9.0727 | 9.9464 | 13.5317 | 16.8751 | 19.8717 | 21.0668 | 23.1276 | 16.5207
2064 | 22.9909 | 20.6407 | 17.2102 | 13.9702 | 9.9444 | 9.0727 | 9.9464 | 13.5317 | 16.8751 | 19.8717 | 21.0668 | 23.1276 | 16.5207
2065 | 23.3113 | 20.8006 | 17.326 | 14.0295 | 9.9068 | 8.975 | 9.8707 | 13.553 | 17.0242 | 19.9311 | 21.1642 | 23.3355 | 16.6023
2066 | 22.8529 | 20.3909 | 16.9674 | 13.9705 | 9.9735 | 9.1037 | 9.9661 | 13.4537 | 16.7912 | 19.7879 | 20.8383 | 23.0565 | 16.4294
2067 | 22.9909 | 20.6407 | 17.2102 | 13.9702 | 9.9444 | 9.0727 | 9.9464 | 13.5317 | 16.8751 | 19.8717 | 21.0668 | 23.1276 | 16.5207
2068 | 22.9909 | 20.6407 | 17.2102 | 13.9702 | 9.9444 | 9.0727 | 9.9464 | 13.5317 | 16.8751 | 19.8717 | 21.0668 | 23.1276 | 16.5207
2069 | 22.9909 | 20.6407 | 17.2102 | 13.9702 | 9.9444 | 9.0727 | 9.9464 | 13.5317 | 16.8751 | 19.8717 | 21.0668 | 23.1276 | 16.5207
2070 | 22.8529 | 20.3909 | 16.9674 | 13.9705 | 9.9735 | 9.1037 | 9.9661 | 13.4537 | 16.7912 | 19.7879 | 20.8383 | 23.0565 | 16.4294
2071 | 22.6941 | 20.2125 | 16.7806 | 14.0257 | 10.0487 | 9.1253 | 9.9902 | 13.4736 | 16.6934 | 19.8067 | 20.8471 | 23.003 | 16.3917
2072 | 22.6941 | 20.2125 | 16.7806 | 14.0257 | 10.0487 | 9.1253 | 9.9902 | 13.4736 | 16.6934 | 19.8067 | 20.8471 | 23.003 | 16.3917
2073 | 22.6941 | 20.2125 | 16.7806 | 14.0257 | 10.0487 | 9.1253 | 9.9902 | 13.4736 | 16.6934 | 19.8067 | 20.8471 | 23.003 | 16.3917
2074 | 22.6941 | 20.2125 | 16.7806 | 14.0257 | 10.0487 | 9.1253 | 9.9902 | 13.4736 | 16.6934 | 19.8067 | 20.8471 | 23.003 | 16.3917
2075 | 22.5556 | 20.1231 | 16.7461 | 14.0359 | 9.9973 | 9.1698 | 9.9642 | 13.4953 | 16.7521 | 19.8593 | 20.8466 | 22.9687 | 16.3762
2076 | 22.6292 | 20.0175 | 16.5411 | 14.01 | 10.0751 | 9.1471 | 9.9858 | 13.4807 | 16.7764 | 19.7992 | 20.8333 | 22.9973 | 16.3577
2077 | 22.6292 | 20.0175 | 16.5411 | 14.01 | 10.0751 | 9.1471 | 9.9858 | 13.4807 | 16.7764 | 19.7992 | 20.8333 | 22.9973 | 16.3577
2079 | 22.5798 | 19.8197 | 16.5612 | 14.024 | 10.0961 | 9.1492 | 9.9856 | 13.5406 | 16.7204 | 19.8417 | 20.7332 | 22.8247 | 16.323
2080 | 22.6432 | 19.9803 | 16.6981 | 14.11 | 10.0358 | 9.1516 | 9.9864 | 13.5396 | 16.7705 | 19.856 | 20.8851 | 22.8499 | 16.3755
2081 | 22.913 | 20.1589 | 16.9239 | 14.2115 | 10.0805 | 9.1093 | 9.9761 | 13.5727 | 16.8734 | 19.9905 | 21.0706 | 23.0012 | 16.4901
2082 | 22.4763 | 19.7015 | 16.7252 | 14.193 | 10.0828 | 9.1298 | 10.0699 | 13.6922 | 16.8394 | 19.9529 | 20.7786 | 22.8415 | 16.3736
2083 | 22.7129 | 20.1694 | 16.9753 | 14.1489 | 10.0059 | 9.0541 | 9.999 | 13.6265 | 16.8417 | 19.987 | 21.0835 | 22.8966 | 16.4584
2084 | 22.834 | 20.2696 | 16.9146 | 14.1578 | 10.0557 | 9.1619 | 9.9821 | 13.6248 | 16.8841 | 19.9174 | 21.056 | 22.9712 | 16.4858
2085 | 22.7737 | 20.4271 | 16.928 | 14.06 | 10.0302 | 9.1696 | 9.9587 | 13.4848 | 16.8343 | 19.9147 | 20.9979 | 22.9794 | 16.4632
2086 | 23.2566 | 21.0136 | 17.3886 | 14.2214 | 9.9934 | 9.0913 | 9.9564 | 13.6089 | 17.0484 | 20.1613 | 21.4131 | 23.26 | 16.7011
2087 | 22.799 | 20.5589 | 17.0113 | 13.9861 | 10.0119 | 9.1121 | 9.9476 | 13.4985 | 16.7501 | 19.8901 | 21.047 | 23.0557 | 16.4723
2088 | 23.6162 | 21.1972 | 17.8055 | 14.3344 | 9.9242 | 8.8767 | 9.8037 | 13.5648 | 17.0928 | 20.2309 | 21.7098 | 23.5883 | 16.812
2089 | 23.3113 | 20.8006 | 17.326 | 14.0295 | 9.9068 | 8.975 | 9.8707 | 13.553 | 17.0242 | 19.9311 | 21.1642 | 23.3355 | 16.6023
2090 | 23.6162 | 21.1972 | 17.8055 | 14.3344 | 9.9242 | 8.8767 | 9.8037 | 13.5648 | 17.0928 | 20.2309 | 21.7098 | 23.5883 | 16.812
2092 | 23.4272 | 21.136 | 17.5755 | 14.2148 | 9.9245 | 8.9936 | 9.9251 | 13.6207 | 17.0441 | 20.2 | 21.5319 | 23.3971 | 16.7492
2093 | 23.4272 | 21.136 | 17.5755 | 14.2148 | 9.9245 | 8.9936 | 9.9251 | 13.6207 | 17.0441 | 20.2 | 21.5319 | 23.3971 | 16.7492
2094 | 23.4272 | 21.136 | 17.5755 | 14.2148 | 9.9245 | 8.9936 | 9.9251 | 13.6207 | 17.0441 | 20.2 | 21.5319 | 23.3971 | 16.7492
2095 | 24.0173 | 21.6535 | 18.1704 | 14.6533 | 10.0151 | 8.8921 | 9.8257 | 13.5848 | 17.1975 | 20.4197 | 22.142 | 23.9384 | 17.0425
2096 | 23.8622 | 21.5942 | 18.0173 | 14.6583 | 10.0114 | 8.99 | 9.8692 | 13.6894 | 17.2782 | 20.343 | 21.955 | 23.6681 | 16.9947
2097 | 23.8622 | 21.5942 | 18.0173 | 14.6583 | 10.0114 | 8.99 | 9.8692 | 13.6894 | 17.2782 | 20.343 | 21.955 | 23.6681 | 16.9947
2099 | 23.2566 | 21.0136 | 17.3886 | 14.2214 | 9.9934 | 9.0913 | 9.9564 | 13.6089 | 17.0484 | 20.1613 | 21.4131 | 23.26 | 16.7011
2100 | 23.2566 | 21.0136 | 17.3886 | 14.2214 | 9.9934 | 9.0913 | 9.9564 | 13.6089 | 17.0484 | 20.1613 | 21.4131 | 23.26 | 16.7011
2101 | 23.195 | 20.8833 | 17.3185 | 14.2867 | 10.0276 | 9.1399 | 9.9666 | 13.6305 | 17.0215 | 20.1834 | 21.2667 | 23.1518 | 16.6726
2102 | 23.7883 | 21.4443 | 17.8189 | 14.7133 | 10.0856 | 9.0766 | 9.9427 | 13.7788 | 17.2653 | 20.2999 | 21.802 | 23.5414 | 16.9631
2103 | 23.7883 | 21.4443 | 17.8189 | 14.7133 | 10.0856 | 9.0766 | 9.9427 | 13.7788 | 17.2653 | 20.2999 | 21.802 | 23.5414 | 16.9631
2104 | 23.1537 | 20.646 | 17.2547 | 14.29 | 10.0475 | 9.1386 | 9.9916 | 13.6422 | 17.0382 | 20.0473 | 21.236 | 23.1053 | 16.6326
2105 | 23.1537 | 20.646 | 17.2547 | 14.29 | 10.0475 | 9.1386 | 9.9916 | 13.6422 | 17.0382 | 20.0473 | 21.236 | 23.1053 | 16.6326
2106 | 23.7883 | 21.4443 | 17.8189 | 14.7133 | 10.0856 | 9.0766 | 9.9427 | 13.7788 | 17.2653 | 20.2999 | 21.802 | 23.5414 | 16.9631
2107 | 23.4726 | 20.9818 | 17.5769 | 14.4703 | 10.1006 | 9.074 | 9.9548 | 13.7399 | 17.2299 | 20.4044 | 21.7915 | 23.507 | 16.8586
2108 | 23.4726 | 20.9818 | 17.5769 | 14.4703 | 10.1006 | 9.074 | 9.9548 | 13.7399 | 17.2299 | 20.4044 | 21.7915 | 23.507 | 16.8586
2109 | 22.691 | 20.0771 | 16.6423 | 14.0026 | 10.0541 | 9.103 | 10.0048 | 13.5061 | 16.7539 | 19.7882 | 20.8144 | 23.1039 | 16.3785
2110 | 23.0637 | 20.5479 | 17.1181 | 14.0026 | 9.9695 | 8.9974 | 9.9116 | 13.5101 | 16.8829 | 19.8155 | 20.988 | 23.216 | 16.5019
2111 | 23.0636 | 20.3346 | 16.8694 | 14.0196 | 9.9857 | 9.0593 | 9.9288 | 13.5092 | 16.7824 | 19.8079 | 20.8672 | 23.2029 | 16.4525
2112 | 22.81 | 20.1552 | 16.7321 | 14.0272 | 10.007 | 9.0967 | 9.9602 | 13.4366 | 16.8286 | 19.7674 | 20.7349 | 23.1458 | 16.3918
2113 | 22.8529 | 20.3909 | 16.9674 | 13.9705 | 9.9735 | 9.1037 | 9.9661 | 13.4537 | 16.7912 | 19.7879 | 20.8383 | 23.0565 | 16.4294
2114 | 22.81 | 20.1552 | 16.7321 | 14.0272 | 10.007 | 9.0967 | 9.9602 | 13.4366 | 16.8286 | 19.7674 | 20.7349 | 23.1458 | 16.3918
2115 | 22.8521 | 20.074 | 16.7415 | 14.0223 | 10.0411 | 9.105 | 9.9974 | 13.4429 | 16.8544 | 19.8282 | 20.917 | 23.2643 | 16.4283
2116 | 22.8521 | 20.074 | 16.7415 | 14.0223 | 10.0411 | 9.105 | 9.9974 | 13.4429 | 16.8544 | 19.8282 | 20.917 | 23.2643 | 16.4283
2117 | 22.8521 | 20.074 | 16.7415 | 14.0223 | 10.0411 | 9.105 | 9.9974 | 13.4429 | 16.8544 | 19.8282 | 20.917 | 23.2643 | 16.4283
2118 | 22.8228 | 20.0627 | 16.6555 | 13.986 | 10.0779 | 9.1143 | 10.0053 | 13.5028 | 16.8106 | 19.8244 | 20.8906 | 23.2457 | 16.4166
2119 | 22.8228 | 20.0627 | 16.6555 | 13.986 | 10.0779 | 9.1143 | 10.0053 | 13.5028 | 16.8106 | 19.8244 | 20.8906 | 23.2457 | 16.4166
2120 | 22.6292 | 20.0175 | 16.5411 | 14.01 | 10.0751 | 9.1471 | 9.9858 | 13.4807 | 16.7764 | 19.7992 | 20.8333 | 22.9973 | 16.3577
2121 | 22.691 | 20.0771 | 16.6423 | 14.0026 | 10.0541 | 9.103 | 10.0048 | 13.5061 | 16.7539 | 19.7882 | 20.8144 | 23.1039 | 16.3785
2122 | 22.81 | 20.1552 | 16.7321 | 14.0272 | 10.007 | 9.0967 | 9.9602 | 13.4366 | 16.8286 | 19.7674 | 20.7349 | 23.1458 | 16.3918
2125 | 22.8228 | 20.0627 | 16.6555 | 13.986 | 10.0779 | 9.1143 | 10.0053 | 13.5028 | 16.8106 | 19.8244 | 20.8906 | 23.2457 | 16.4166
2126 | 22.7357 | 20.0543 | 16.5466 | 13.9717 | 10.0729 | 9.1347 | 9.9806 | 13.5059 | 16.8086 | 19.8564 | 20.882 | 23.1577 | 16.3923
2127 | 23.0434 | 20.2108 | 16.782 | 13.9773 | 10.047 | 9.0917 | 9.9251 | 13.4871 | 16.7771 | 19.8223 | 20.9446 | 23.2838 | 16.4493
2128 | 23.0434 | 20.2108 | 16.782 | 13.9773 | 10.047 | 9.0917 | 9.9251 | 13.4871 | 16.7771 | 19.8223 | 20.9446 | 23.2838 | 16.4493
2129 | 23.0434 | 20.2108 | 16.782 | 13.9773 | 10.047 | 9.0917 | 9.9251 | 13.4871 | 16.7771 | 19.8223 | 20.9446 | 23.2838 | 16.4493
2130 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2131 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2132 | 23.294 | 20.5417 | 17.1062 | 14.0007 | 10.0662 | 9.0703 | 9.9193 | 13.4992 | 16.8407 | 19.9477 | 21.063 | 23.529 | 16.5732
2133 | 23.294 | 20.5417 | 17.1062 | 14.0007 | 10.0662 | 9.0703 | 9.9193 | 13.4992 | 16.8407 | 19.9477 | 21.063 | 23.529 | 16.5732
2134 | 23.294 | 20.5417 | 17.1062 | 14.0007 | 10.0662 | 9.0703 | 9.9193 | 13.4992 | 16.8407 | 19.9477 | 21.063 | 23.529 | 16.5732
2135 | 23.294 | 20.5417 | 17.1062 | 14.0007 | 10.0662 | 9.0703 | 9.9193 | 13.4992 | 16.8407 | 19.9477 | 21.063 | 23.529 | 16.5732
2136 | 23.2008 | 20.4381 | 17.0527 | 13.9573 | 10.1082 | 9.1299 | 9.9714 | 13.5197 | 16.851 | 19.9143 | 21.0187 | 23.5616 | 16.5603
2137 | 23.0636 | 20.3346 | 16.8694 | 14.0196 | 9.9857 | 9.0593 | 9.9288 | 13.5092 | 16.7824 | 19.8079 | 20.8672 | 23.2029 | 16.4525
2138 | 23.0636 | 20.3346 | 16.8694 | 14.0196 | 9.9857 | 9.0593 | 9.9288 | 13.5092 | 16.7824 | 19.8079 | 20.8672 | 23.2029 | 16.4525
2139 | 23.0636 | 20.3346 | 16.8694 | 14.0196 | 9.9857 | 9.0593 | 9.9288 | 13.5092 | 16.7824 | 19.8079 | 20.8672 | 23.2029 | 16.4525
2140 | 23.0636 | 20.3346 | 16.8694 | 14.0196 | 9.9857 | 9.0593 | 9.9288 | 13.5092 | 16.7824 | 19.8079 | 20.8672 | 23.2029 | 16.4525
2141 | 23.0434 | 20.2108 | 16.782 | 13.9773 | 10.047 | 9.0917 | 9.9251 | 13.4871 | 16.7771 | 19.8223 | 20.9446 | 23.2838 | 16.4493
2142 | 22.9826 | 20.1117 | 16.8186 | 13.9864 | 10.0847 | 9.1109 | 9.9599 | 13.4374 | 16.8208 | 19.8424 | 20.9731 | 23.4318 | 16.4634
2143 | 23.2008 | 20.4381 | 17.0527 | 13.9573 | 10.1082 | 9.1299 | 9.9714 | 13.5197 | 16.851 | 19.9143 | 21.0187 | 23.5616 | 16.5603
2144 | 23.0434 | 20.2108 | 16.782 | 13.9773 | 10.047 | 9.0917 | 9.9251 | 13.4871 | 16.7771 | 19.8223 | 20.9446 | 23.2838 | 16.4493
2145 | 22.9198 | 19.9927 | 16.8414 | 14.0131 | 10.1188 | 9.1197 | 10.0257 | 13.4942 | 16.8839 | 19.893 | 20.9072 | 23.5347 | 16.4787
2146 | 22.9198 | 19.9927 | 16.8414 | 14.0131 | 10.1188 | 9.1197 | 10.0257 | 13.4942 | 16.8839 | 19.893 | 20.9072 | 23.5347 | 16.4787
2147 | 22.9559 | 19.7909 | 16.8447 | 14.0381 | 10.1514 | 9.1351 | 10.0694 | 13.4742 | 16.8659 | 19.8268 | 20.8858 | 23.2717 | 16.4425
2148 | 22.9297 | 19.8445 | 16.8578 | 14.0131 | 10.2135 | 9.1206 | 10.0719 | 13.5327 | 16.8936 | 19.9001 | 20.8967 | 23.3661 | 16.47
2150 | 22.9301 | 20.0165 | 16.8116 | 14.0181 | 10.0748 | 9.1054 | 10.0268 | 13.4754 | 16.8398 | 19.8855 | 20.9809 | 23.4312 | 16.4663
2151 | 22.9301 | 20.0165 | 16.8116 | 14.0181 | 10.0748 | 9.1054 | 10.0268 | 13.4754 | 16.8398 | 19.8855 | 20.9809 | 23.4312 | 16.4663
2152 | 22.9301 | 20.0165 | 16.8116 | 14.0181 | 10.0748 | 9.1054 | 10.0268 | 13.4754 | 16.8398 | 19.8855 | 20.9809 | 23.4312 | 16.4663
2153 | 22.9557 | 19.9373 | 16.7228 | 14.027 | 10.104 | 9.1341 | 10.0277 | 13.505 | 16.8483 | 19.882 | 20.8791 | 23.2819 | 16.4421
2154 | 22.9557 | 19.9373 | 16.7228 | 14.027 | 10.104 | 9.1341 | 10.0277 | 13.505 | 16.8483 | 19.882 | 20.8791 | 23.2819 | 16.4421
2155 | 22.8251 | 19.7838 | 16.7845 | 14.0104 | 10.1605 | 9.1282 | 10.0481 | 13.5173 | 16.8515 | 19.8383 | 20.8514 | 23.1133 | 16.4094
2156 | 22.6248 | 19.7917 | 16.6541 | 13.9611 | 10.1867 | 9.0673 | 10.0694 | 13.5739 | 16.7954 | 19.9013 | 20.7476 | 22.8951 | 16.3557
2157 | 22.4693 | 19.5918 | 16.5026 | 14.0048 | 10.1248 | 9.1115 | 10.0716 | 13.7036 | 16.8658 | 19.9277 | 20.7208 | 22.8642 | 16.3299
2158 | 22.7357 | 20.0543 | 16.5466 | 13.9717 | 10.0729 | 9.1347 | 9.9806 | 13.5059 | 16.8086 | 19.8564 | 20.882 | 23.1577 | 16.3923
2159 | 22.6413 | 19.7658 | 16.5097 | 13.9198 | 10.1272 | 9.1565 | 10.0133 | 13.5266 | 16.7383 | 19.8021 | 20.7285 | 22.8916 | 16.3184
2160 | 22.9826 | 20.1117 | 16.8186 | 13.9864 | 10.0847 | 9.1109 | 9.9599 | 13.4374 | 16.8208 | 19.8424 | 20.9731 | 23.4318 | 16.4634
2161 | 22.9826 | 20.1117 | 16.8186 | 13.9864 | 10.0847 | 9.1109 | 9.9599 | 13.4374 | 16.8208 | 19.8424 | 20.9731 | 23.4318 | 16.4634
2162 | 22.9953 | 20.2592 | 16.966 | 13.8883 | 10.098 | 9.1164 | 10.006 | 13.4725 | 16.8769 | 19.9149 | 21.0568 | 23.5638 | 16.5178
2163 | 22.9953 | 20.2592 | 16.966 | 13.8883 | 10.098 | 9.1164 | 10.006 | 13.4725 | 16.8769 | 19.9149 | 21.0568 | 23.5638 | 16.5178
2164 | 22.8165 | 19.9928 | 16.8587 | 14.0166 | 10.1651 | 9.0795 | 9.9977 | 13.5273 | 16.9219 | 19.8971 | 21.0183 | 23.5091 | 16.4834
2165 | 22.882 | 20.1327 | 16.8541 | 13.9946 | 10.1189 | 9.1257 | 10.0236 | 13.4516 | 16.9028 | 19.8818 | 20.9685 | 23.5202 | 16.488
2166 | 22.8024 | 20.2146 | 16.9072 | 13.9577 | 10.0813 | 9.083 | 9.9831 | 13.4892 | 16.9578 | 19.9759 | 20.9823 | 23.5218 | 16.4964
2167 | 22.8539 | 20.1954 | 17.0265 | 13.9794 | 10.1455 | 9.0761 | 10.0385 | 13.5661 | 16.952 | 20.0149 | 20.8721 | 23.5604 | 16.5234
2168 | 22.8215 | 20.0649 | 16.9271 | 14.0368 | 10.1675 | 9.0631 | 10.0197 | 13.5223 | 16.8961 | 19.9414 | 20.8485 | 23.515 | 16.4853
2170 | 22.8539 | 20.1954 | 17.0265 | 13.9794 | 10.1455 | 9.0761 | 10.0385 | 13.5661 | 16.952 | 20.0149 | 20.8721 | 23.5604 | 16.5234
2171 | 22.8689 | 20.1105 | 16.9028 | 13.9903 | 10.2072 | 9.0345 | 10.0329 | 13.6209 | 16.9558 | 20.0191 | 20.8953 | 23.5475 | 16.5155
2172 | 23.0541 | 20.3259 | 17.2031 | 13.8568 | 10.1227 | 9.1267 | 10.0301 | 13.507 | 16.9348 | 20.0913 | 21.1766 | 23.7043 | 16.5944
2173 | 22.9536 | 20.1442 | 17.2626 | 13.9184 | 10.0931 | 8.9872 | 9.9824 | 13.4229 | 17.0061 | 20.0672 | 21.2454 | 23.5733 | 16.5547
2174 | 22.8689 | 20.1105 | 16.9028 | 13.9903 | 10.2072 | 9.0345 | 10.0329 | 13.6209 | 16.9558 | 20.0191 | 20.8953 | 23.5475 | 16.5155
2175 | 22.7428 | 19.8854 | 16.7754 | 14.0132 | 10.226 | 9.0583 | 10.0615 | 13.6062 | 16.9442 | 19.8554 | 20.9583 | 23.4205 | 16.4623
2176 | 22.8165 | 19.9928 | 16.8587 | 14.0166 | 10.1651 | 9.0795 | 9.9977 | 13.5273 | 16.9219 | 19.8971 | 21.0183 | 23.5091 | 16.4834
2177 | 22.8215 | 20.0649 | 16.9271 | 14.0368 | 10.1675 | 9.0631 | 10.0197 | 13.5223 | 16.8961 | 19.9414 | 20.8485 | 23.515 | 16.4853
2178 | 22.6852 | 19.7546 | 16.8014 | 14.0125 | 10.229 | 9.0421 | 10.105 | 13.5632 | 16.9288 | 19.8241 | 20.8804 | 23.2996 | 16.4272
2179 | 22.8253 | 20.0035 | 16.861 | 14.0851 | 10.2475 | 9.0063 | 10.0837 | 13.5789 | 16.8809 | 20.0152 | 20.9484 | 23.5438 | 16.5066
2190 | 23.2008 | 20.4381 | 17.0527 | 13.9573 | 10.1082 | 9.1299 | 9.9714 | 13.5197 | 16.851 | 19.9143 | 21.0187 | 23.5616 | 16.5603
2191 | 23.294 | 20.5417 | 17.1062 | 14.0007 | 10.0662 | 9.0703 | 9.9193 | 13.4992 | 16.8407 | 19.9477 | 21.063 | 23.529 | 16.5732
2192 | 23.294 | 20.5417 | 17.1062 | 14.0007 | 10.0662 | 9.0703 | 9.9193 | 13.4992 | 16.8407 | 19.9477 | 21.063 | 23.529 | 16.5732
2193 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2194 | 23.294 | 20.5417 | 17.1062 | 14.0007 | 10.0662 | 9.0703 | 9.9193 | 13.4992 | 16.8407 | 19.9477 | 21.063 | 23.529 | 16.5732
2195 | 23.2008 | 20.4381 | 17.0527 | 13.9573 | 10.1082 | 9.1299 | 9.9714 | 13.5197 | 16.851 | 19.9143 | 21.0187 | 23.5616 | 16.5603
2196 | 23.2503 | 20.5623 | 17.2715 | 13.9202 | 10.1176 | 9.143 | 10.0214 | 13.5103 | 16.9735 | 20.1452 | 21.2526 | 23.7395 | 16.659
2197 | 22.9953 | 20.2592 | 16.966 | 13.8883 | 10.098 | 9.1164 | 10.006 | 13.4725 | 16.8769 | 19.9149 | 21.0568 | 23.5638 | 16.5178
2198 | 22.9953 | 20.2592 | 16.966 | 13.8883 | 10.098 | 9.1164 | 10.006 | 13.4725 | 16.8769 | 19.9149 | 21.0568 | 23.5638 | 16.5178
2199 | 22.9953 | 20.2592 | 16.966 | 13.8883 | 10.098 | 9.1164 | 10.006 | 13.4725 | 16.8769 | 19.9149 | 21.0568 | 23.5638 | 16.5178
2200 | 22.9953 | 20.2592 | 16.966 | 13.8883 | 10.098 | 9.1164 | 10.006 | 13.4725 | 16.8769 | 19.9149 | 21.0568 | 23.5638 | 16.5178
2203 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2204 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2205 | 23.5618 | 20.9718 | 17.4553 | 13.926 | 9.9911 | 9.0098 | 9.8752 | 13.4268 | 16.9158 | 20.1852 | 21.2557 | 23.762 | 16.6947
2206 | 23.3365 | 20.6475 | 17.2737 | 14.023 | 9.9581 | 9.0091 | 9.8532 | 13.4431 | 16.9098 | 19.9275 | 21.1445 | 23.4673 | 16.5828
2207 | 23.4738 | 20.7919 | 17.3496 | 13.8887 | 10.0811 | 9.0713 | 9.9544 | 13.4889 | 16.9201 | 20.1636 | 21.257 | 23.8121 | 16.6877
2208 | 23.4738 | 20.7919 | 17.3496 | 13.8887 | 10.0811 | 9.0713 | 9.9544 | 13.4889 | 16.9201 | 20.1636 | 21.257 | 23.8121 | 16.6877
2209 | 23.4738 | 20.7919 | 17.3496 | 13.8887 | 10.0811 | 9.0713 | 9.9544 | 13.4889 | 16.9201 | 20.1636 | 21.257 | 23.8121 | 16.6877
2210 | 23.2503 | 20.5623 | 17.2715 | 13.9202 | 10.1176 | 9.143 | 10.0214 | 13.5103 | 16.9735 | 20.1452 | 21.2526 | 23.7395 | 16.659
2211 | 23.2503 | 20.5623 | 17.2715 | 13.9202 | 10.1176 | 9.143 | 10.0214 | 13.5103 | 16.9735 | 20.1452 | 21.2526 | 23.7395 | 16.659
2212 | 23.0541 | 20.3259 | 17.2031 | 13.8568 | 10.1227 | 9.1267 | 10.0301 | 13.507 | 16.9348 | 20.0913 | 21.1766 | 23.7043 | 16.5944
2213 | 23.0541 | 20.3259 | 17.2031 | 13.8568 | 10.1227 | 9.1267 | 10.0301 | 13.507 | 16.9348 | 20.0913 | 21.1766 | 23.7043 | 16.5944
2214 | 23.0541 | 20.3259 | 17.2031 | 13.8568 | 10.1227 | 9.1267 | 10.0301 | 13.507 | 16.9348 | 20.0913 | 21.1766 | 23.7043 | 16.5944
2216 | 23.5618 | 20.9718 | 17.4553 | 13.926 | 9.9911 | 9.0098 | 9.8752 | 13.4268 | 16.9158 | 20.1852 | 21.2557 | 23.762 | 16.6947
2217 | 23.5618 | 20.9718 | 17.4553 | 13.926 | 9.9911 | 9.0098 | 9.8752 | 13.4268 | 16.9158 | 20.1852 | 21.2557 | 23.762 | 16.6947
2218 | 23.4738 | 20.7919 | 17.3496 | 13.8887 | 10.0811 | 9.0713 | 9.9544 | 13.4889 | 16.9201 | 20.1636 | 21.257 | 23.8121 | 16.6877
2219 | 23.5807 | 21.14 | 17.7334 | 14.0325 | 9.8478 | 8.8646 | 9.7989 | 13.5045 | 17.0863 | 20.2523 | 21.4473 | 23.7933 | 16.7568
2220 | 23.4738 | 20.7919 | 17.3496 | 13.8887 | 10.0811 | 9.0713 | 9.9544 | 13.4889 | 16.9201 | 20.1636 | 21.257 | 23.8121 | 16.6877
2221 | 23.5811 | 20.9653 | 17.4934 | 14.0083 | 9.9278 | 8.9708 | 9.9529 | 13.5146 | 17.094 | 20.2728 | 21.4186 | 23.8937 | 16.7578
2222 | 23.4738 | 20.7919 | 17.3496 | 13.8887 | 10.0811 | 9.0713 | 9.9544 | 13.4889 | 16.9201 | 20.1636 | 21.257 | 23.8121 | 16.6877
2223 | 23.3871 | 20.6868 | 17.4622 | 13.9404 | 10.0209 | 9.0864 | 10.003 | 13.4913 | 17.0623 | 20.273 | 21.4341 | 23.8056 | 16.7211
2224 | 23.5811 | 20.9653 | 17.4934 | 14.0083 | 9.9278 | 8.9708 | 9.9529 | 13.5146 | 17.094 | 20.2728 | 21.4186 | 23.8937 | 16.7578
2225 | 23.5811 | 20.9653 | 17.4934 | 14.0083 | 9.9278 | 8.9708 | 9.9529 | 13.5146 | 17.094 | 20.2728 | 21.4186 | 23.8937 | 16.7578
2226 | 23.3871 | 20.6868 | 17.4622 | 13.9404 | 10.0209 | 9.0864 | 10.003 | 13.4913 | 17.0623 | 20.273 | 21.4341 | 23.8056 | 16.7211
2227 | 23.6348 | 20.9867 | 17.7475 | 14.0708 | 9.9501 | 8.9101 | 9.8885 | 13.5467 | 17.2511 | 20.327 | 21.5952 | 23.8921 | 16.8167
2228 | 23.6348 | 20.9867 | 17.7475 | 14.0708 | 9.9501 | 8.9101 | 9.8885 | 13.5467 | 17.2511 | 20.327 | 21.5952 | 23.8921 | 16.8167
2229 | 23.6348 | 20.9867 | 17.7475 | 14.0708 | 9.9501 | 8.9101 | 9.8885 | 13.5467 | 17.2511 | 20.327 | 21.5952 | 23.8921 | 16.8167
2230 | 23.7783 | 21.1951 | 17.9537 | 14.1865 | 9.862 | 8.7708 | 9.7794 | 13.429 | 17.2028 | 20.3588 | 21.6935 | 24.057 | 16.8556
2231 | 24.1921 | 21.4759 | 18.1821 | 14.2291 | 9.9188 | 8.6934 | 9.6876 | 13.3534 | 17.1397 | 20.5485 | 21.9705 | 24.223 | 16.9678
2232 | 23.4398 | 20.7594 | 17.577 | 13.9807 | 10.0447 | 9.0351 | 10.0045 | 13.504 | 17.0779 | 20.2478 | 21.4811 | 23.8353 | 16.7489
2233 | 23.4407 | 20.8352 | 17.4796 | 13.9908 | 10.042 | 8.9693 | 9.9972 | 13.6062 | 17.1814 | 20.2574 | 21.4826 | 23.8788 | 16.7634
2234 | 23.0578 | 20.3918 | 17.3864 | 13.8907 | 10.0442 | 9.0997 | 10.0325 | 13.4586 | 17.0424 | 20.1782 | 21.357 | 23.6735 | 16.6344
2250 | 22.4609 | 19.8049 | 16.5211 | 14.1262 | 10.2027 | 9.1827 | 10.072 | 13.6203 | 16.8272 | 19.834 | 20.78 | 22.7281 | 16.3467
2251 | 23.5886 | 21.4589 | 17.6123 | 14.4388 | 10.0845 | 9.0822 | 9.943 | 13.7732 | 17.3041 | 20.4848 | 21.8874 | 23.5106 | 16.9307
2256 | 22.6889 | 20.2892 | 16.9189 | 13.9596 | 9.9981 | 9.154 | 10.0026 | 13.6361 | 16.8724 | 20.0253 | 20.9866 | 22.7844 | 16.443
2257 | 22.9503 | 20.5903 | 17.0421 | 14.0838 | 10.0523 | 9.1484 | 9.9362 | 13.6923 | 17.0323 | 20.1109 | 21.1899 | 22.9429 | 16.5643
2258 | 22.4985 | 20.1477 | 16.7493 | 14.1765 | 10.2568 | 9.2807 | 10.0962 | 13.7921 | 17.0609 | 19.9475 | 20.7368 | 22.6157 | 16.4466
2259 | 22.0695 | 19.7373 | 16.5335 | 14.1272 | 10.2725 | 9.2789 | 10.0594 | 13.6882 | 16.8992 | 19.7435 | 20.5872 | 22.2925 | 16.2741
2260 | 23.7882 | 21.6586 | 17.9851 | 14.7501 | 10.1358 | 9.0309 | 9.9909 | 13.8169 | 17.407 | 20.4176 | 22.1197 | 23.7405 | 17.0701
2261 | 23.5419 | 21.1429 | 17.9149 | 14.7014 | 10.1567 | 9.0729 | 9.9211 | 13.8398 | 17.3764 | 20.2284 | 21.627 | 23.2463 | 16.8975
2262 | 23.6022 | 21.3592 | 18.022 | 14.6279 | 10.3253 | 9.1841 | 10.0321 | 13.7464 | 17.3187 | 20.4202 | 21.7558 | 23.6781 | 17.006
2263 | 23.8731 | 21.5138 | 18.1796 | 14.7753 | 10.3179 | 9.1202 | 10.0306 | 13.8223 | 17.3939 | 20.5997 | 22.0805 | 23.7928 | 17.125
2264 | 22.3248 | 20.035 | 16.8018 | 14.2394 | 10.2768 | 9.2741 | 10.0374 | 13.761 | 16.9959 | 19.9352 | 20.6462 | 22.3396 | 16.3889
2265 | 22.47 | 20.0416 | 16.7722 | 14.2136 | 10.257 | 9.3132 | 10.1226 | 13.8336 | 17.0106 | 20.0562 | 20.8379 | 22.6424 | 16.4642
2267 | 23.4199 | 21.1109 | 17.9003 | 14.5735 | 10.3093 | 9.2104 | 10.0652 | 13.9082 | 17.2308 | 20.4931 | 21.8287 | 23.355 | 16.9504
2278 | 23.2215 | 20.7359 | 17.1965 | 14.3917 | 10.4241 | 9.3664 | 10.1691 | 13.9547 | 17.0734 | 20.2216 | 21.4856 | 23.4324 | 16.8061
2280 | 23.8614 | 21.4853 | 17.865 | 14.4164 | 10.2731 | 9.2712 | 10.1301 | 13.9815 | 17.2752 | 20.5916 | 22.0558 | 23.7856 | 17.0827
2281 | 24.1614 | 21.6304 | 18.3362 | 14.7537 | 10.3449 | 9.1425 | 10.0946 | 13.8974 | 17.436 | 20.8415 | 22.4459 | 24.2058 | 17.2742
2282 | 23.8614 | 21.4853 | 17.865 | 14.4164 | 10.2731 | 9.2712 | 10.1301 | 13.9815 | 17.2752 | 20.5916 | 22.0558 | 23.7856 | 17.0827
2283 | 23.078 | 20.608 | 17.2435 | 14.4009 | 10.3161 | 9.3509 | 10.161 | 13.9357 | 17.0817 | 20.2211 | 21.2694 | 23.0522 | 16.7265
2284 | 23.3675 | 21.0205 | 17.3823 | 14.4787 | 10.4624 | 9.4178 | 10.1693 | 13.9306 | 17.1417 | 20.3192 | 21.7009 | 23.4684 | 16.9049
2285 | 23.6487 | 21.4206 | 17.5777 | 14.4889 | 10.4694 | 9.4327 | 10.1568 | 13.9729 | 17.333 | 20.4112 | 21.8308 | 23.868 | 17.0509
2286 | 23.358 | 21.0631 | 17.3529 | 14.5551 | 10.4934 | 9.4509 | 10.1629 | 13.905 | 17.1358 | 20.3671 | 21.7646 | 23.7577 | 16.9472
2287 | 23.6487 | 21.4206 | 17.5777 | 14.4889 | 10.4694 | 9.4327 | 10.1568 | 13.9729 | 17.333 | 20.4112 | 21.8308 | 23.868 | 17.0509
2289 | 24.0656 | 21.7236 | 17.9794 | 14.5774 | 10.3505 | 9.329 | 10.1333 | 14.0303 | 17.4089 | 20.6342 | 22.0105 | 24.0749 | 17.1931
2290 | 24.2353 | 21.8468 | 18.1344 | 14.7295 | 10.3106 | 9.1816 | 10.0974 | 14.0743 | 17.4222 | 20.7079 | 22.2126 | 24.105 | 17.2548
2291 | 24.422 | 21.9235 | 18.3693 | 14.8992 | 10.3648 | 9.1771 | 9.993 | 14.0113 | 17.5019 | 20.6424 | 22.2995 | 24.334 | 17.3282
2292 | 24.15 | 21.6383 | 18.2058 | 14.7033 | 10.3088 | 9.2095 | 9.9668 | 13.9633 | 17.3976 | 20.5263 | 22.1556 | 24.2073 | 17.2027
2293 | 24.15 | 21.6383 | 18.2058 | 14.7033 | 10.3088 | 9.2095 | 9.9668 | 13.9633 | 17.3976 | 20.5263 | 22.1556 | 24.2073 | 17.2027
2294 | 24.15 | 21.6383 | 18.2058 | 14.7033 | 10.3088 | 9.2095 | 9.9668 | 13.9633 | 17.3976 | 20.5263 | 22.1556 | 24.2073 | 17.2027
2295 | 24.1386 | 21.7254 | 18.0765 | 14.4198 | 10.2968 | 9.1861 | 9.9731 | 13.9247 | 17.1906 | 20.5528 | 22.1581 | 24.3252 | 17.164
2296 | 24.15 | 21.6383 | 18.2058 | 14.7033 | 10.3088 | 9.2095 | 9.9668 | 13.9633 | 17.3976 | 20.5263 | 22.1556 | 24.2073 | 17.2027
2297 | 24.15 | 21.6383 | 18.2058 | 14.7033 | 10.3088 | 9.2095 | 9.9668 | 13.9633 | 17.3976 | 20.5263 | 22.1556 | 24.2073 | 17.2027
2298 | 23.8547 | 21.6082 | 17.9044 | 14.5422 | 10.3858 | 9.3359 | 10.0691 | 14.0234 | 17.4298 | 20.4455 | 21.8161 | 23.964 | 17.1149
2299 | 23.8547 | 21.6082 | 17.9044 | 14.5422 | 10.3858 | 9.3359 | 10.0691 | 14.0234 | 17.4298 | 20.4455 | 21.8161 | 23.964 | 17.1149
2300 | 24.422 | 21.9235 | 18.3693 | 14.8992 | 10.3648 | 9.1771 | 9.993 | 14.0113 | 17.5019 | 20.6424 | 22.2995 | 24.334 | 17.3282
2302 | 24.422 | 21.9235 | 18.3693 | 14.8992 | 10.3648 | 9.1771 | 9.993 | 14.0113 | 17.5019 | 20.6424 | 22.2995 | 24.334 | 17.3282
2303 | 24.422 | 21.9235 | 18.3693 | 14.8992 | 10.3648 | 9.1771 | 9.993 | 14.0113 | 17.5019 | 20.6424 | 22.2995 | 24.334 | 17.3282
2304 | 24.15 | 21.6383 | 18.2058 | 14.7033 | 10.3088 | 9.2095 | 9.9668 | 13.9633 | 17.3976 | 20.5263 | 22.1556 | 24.2073 | 17.2027
2305 | 24.0656 | 21.7236 | 17.9794 | 14.5774 | 10.3505 | 9.329 | 10.1333 | 14.0303 | 17.4089 | 20.6342 | 22.0105 | 24.0749 | 17.1931
2306 | 24.2353 | 21.8468 | 18.1344 | 14.7295 | 10.3106 | 9.1816 | 10.0974 | 14.0743 | 17.4222 | 20.7079 | 22.2126 | 24.105 | 17.2548
2307 | 23.7913 | 21.489 | 17.6867 | 14.4126 | 10.3686 | 9.2685 | 10.0269 | 14.0514 | 17.3791 | 20.3863 | 21.761 | 23.9941 | 17.0513
2308 | 23.8547 | 21.6082 | 17.9044 | 14.5422 | 10.3858 | 9.3359 | 10.0691 | 14.0234 | 17.4298 | 20.4455 | 21.8161 | 23.964 | 17.1149
2311 | 22.6445 | 19.6518 | 16.364 | 14.0863 | 10.1326 | 9.0262 | 9.7429 | 13.6099 | 17.1581 | 20.0309 | 20.3457 | 22.9884 | 16.3151
2312 | 22.6367 | 20.4305 | 17.2801 | 14.7299 | 10.851 | 9.667 | 10.4785 | 14.098 | 17.7165 | 19.8541 | 21.0327 | 23.1234 | 16.8249
2314 | 23.9337 | 21.3429 | 17.8659 | 14.3254 | 10.254 | 9.2502 | 9.9403 | 13.8892 | 17.097 | 20.4603 | 21.7997 | 24.0132 | 17.0143
2315 | 24.3025 | 21.877 | 18.4878 | 14.8548 | 10.1911 | 8.9699 | 9.8087 | 13.7364 | 17.5172 | 20.713 | 22.3035 | 24.4971 | 17.2716
2316 | 23.8019 | 21.511 | 18.0836 | 14.5458 | 10.1438 | 9.0334 | 9.832 | 13.7081 | 17.2155 | 20.4122 | 22.0404 | 23.9763 | 17.0253
2317 | 23.9261 | 21.6529 | 18.2522 | 14.6457 | 10.1674 | 8.9842 | 9.8192 | 13.7244 | 17.4173 | 20.5374 | 22.0633 | 24.1024 | 17.1077
2318 | 23.5206 | 21.241 | 17.7409 | 14.4421 | 10.2276 | 9.2681 | 9.9857 | 13.915 | 17.2541 | 20.4625 | 21.5144 | 23.6575 | 16.9358
2319 | 23.7818 | 21.399 | 17.9547 | 14.553 | 10.1575 | 9.1509 | 9.8393 | 13.7217 | 17.1542 | 20.3326 | 21.8184 | 23.9318 | 16.9829
2320 | 23.3454 | 20.7616 | 17.3241 | 14.6958 | 10.6673 | 9.4751 | 10.35 | 13.9592 | 17.1932 | 20.3014 | 21.6527 | 24.3003 | 17.0022
2321 | 22.9119 | 20.34 | 17.0571 | 14.3945 | 10.3821 | 9.4265 | 9.9709 | 13.8818 | 17.2831 | 20.1457 | 21.3375 | 23.4167 | 16.7123
2322 | 23.7146 | 21.3734 | 17.8379 | 14.5185 | 10.3395 | 9.2065 | 9.9746 | 13.972 | 17.3681 | 20.3693 | 21.7335 | 23.8864 | 17.0245
2323 | 23.365 | 20.8825 | 17.3615 | 14.4575 | 10.404 | 9.3931 | 10.1416 | 13.9772 | 17.2005 | 20.3681 | 21.8499 | 23.9766 | 16.9481
2324 | 23.0396 | 20.4416 | 17.3142 | 14.4127 | 10.4051 | 9.3655 | 10.0078 | 13.885 | 17.2598 | 20.0595 | 21.3331 | 23.4501 | 16.7478
2325 | 22.5832 | 19.9731 | 16.7402 | 14.3072 | 10.3648 | 9.4563 | 10.2872 | 13.9166 | 16.9333 | 20.0752 | 21.0439 | 23.1377 | 16.5682
2326 | 23.2669 | 20.6779 | 17.1934 | 14.5501 | 10.5827 | 9.378 | 10.1579 | 13.9637 | 17.2271 | 20.3141 | 21.6906 | 23.8712 | 16.9061
2327 | 23.3039 | 20.7081 | 17.2422 | 14.4295 | 10.5003 | 9.4361 | 10.1713 | 13.9555 | 17.1983 | 20.284 | 21.828 | 23.8742 | 16.9109
2328 | 24.1502 | 20.8264 | 17.8098 | 14.9606 | 10.8622 | 9.4725 | 10.4222 | 14.189 | 17.6069 | 20.848 | 22.2541 | 25.4205 | 17.4019
2329 | 25.1425 | 21.5726 | 18.8651 | 15.1531 | 11.068 | 9.3841 | 10.5056 | 13.9718 | 17.8448 | 21.3901 | 23.0597 | 26.4081 | 17.8638
2330 | 23.497 | 20.4933 | 17.4969 | 14.8056 | 10.9245 | 9.6943 | 10.5682 | 14.1491 | 17.5663 | 20.614 | 21.8724 | 24.6081 | 17.1908
2333 | 24.9816 | 21.6433 | 18.5826 | 15.0178 | 10.9413 | 9.5451 | 10.4696 | 14.3461 | 17.7646 | 21.1767 | 22.9487 | 26.0393 | 17.7881
2334 | 23.4475 | 20.7579 | 17.2589 | 14.4849 | 10.5978 | 9.3965 | 10.2645 | 13.9736 | 17.2008 | 20.5201 | 21.8717 | 24.3403 | 17.0095
2335 | 23.5152 | 20.7055 | 17.3417 | 14.5313 | 10.4955 | 9.3847 | 10.1915 | 13.9964 | 17.3205 | 20.5538 | 21.8958 | 24.5774 | 17.0424
2336 | 25.075 | 21.5711 | 18.5938 | 14.9177 | 10.4127 | 8.9975 | 9.916 | 13.7489 | 17.1685 | 20.8591 | 22.6738 | 26.1704 | 17.5087
2337 | 24.7885 | 21.4141 | 18.4447 | 14.912 | 10.8099 | 9.1013 | 10.1273 | 13.8664 | 17.7211 | 20.7722 | 22.2394 | 25.7149 | 17.4927
2338 | 25.3078 | 21.5051 | 18.8946 | 15.1285 | 10.915 | 9.1919 | 10.0498 | 13.7477 | 17.6002 | 20.5976 | 21.9439 | 25.9708 | 17.5711
2339 | 26.6649 | 23.3883 | 20.5819 | 16.0496 | 11.7771 | 10.0121 | 10.8608 | 14.5993 | 18.0559 | 21.6293 | 23.6665 | 27.3856 | 18.7226
2340 | 26.5532 | 23.1873 | 20.4187 | 16.1057 | 12.0485 | 10.1509 | 10.961 | 14.6395 | 18.5849 | 21.8076 | 23.9867 | 27.3043 | 18.8124
2341 | 26.6266 | 23.3085 | 20.5582 | 16.1701 | 11.9781 | 10.1664 | 11.1038 | 14.5897 | 18.4708 | 21.7764 | 23.7777 | 27.2118 | 18.8115
2342 | 26.6089 | 23.4425 | 20.8226 | 16.3478 | 12.1146 | 10.3607 | 11.2371 | 14.7846 | 18.7239 | 21.6617 | 23.9681 | 27.4421 | 18.9596
2343 | 26.8994 | 23.6168 | 20.7557 | 16.1827 | 12.0719 | 10.2349 | 11.1014 | 14.6402 | 18.3337 | 21.9116 | 23.9747 | 27.3374 | 18.9217
2344 | 26.6297 | 23.2196 | 20.8048 | 16.3895 | 12.2441 | 10.4435 | 11.3449 | 14.949 | 18.6544 | 21.9605 | 24.1632 | 27.4593 | 19.0219
2345 | 26.318 | 23.0234 | 20.5408 | 16.3866 | 12.1738 | 10.4022 | 11.2973 | 14.7869 | 18.7637 | 21.7666 | 23.7199 | 27.1673 | 18.8622
2346 | 26.0093 | 22.9885 | 20.493 | 16.3461 | 12.3881 | 10.6375 | 11.6182 | 15.027 | 19.0346 | 21.9196 | 23.8459 | 26.8788 | 18.9322
2347 | 26.2036 | 23.0614 | 20.8807 | 16.6342 | 12.5492 | 10.8488 | 11.7687 | 15.274 | 19.3262 | 22.2277 | 24.1026 | 26.8528 | 19.1442
2350 | 23.9284 | 20.7763 | 18.3467 | 15.7085 | 11.578 | 10.2855 | 11.2982 | 14.8056 | 18.6867 | 21.2687 | 21.8762 | 24.6295 | 17.7657
2351 | 24.9849 | 21.4469 | 19.3425 | 16.0242 | 11.7256 | 10.276 | 11.2539 | 14.8383 | 18.8534 | 21.7735 | 22.5538 | 25.953 | 18.2522
2352 | 25.9081 | 22.2767 | 20.104 | 16.0636 | 11.6895 | 9.819 | 10.6947 | 14.3999 | 18.2066 | 21.2304 | 22.9289 | 26.5965 | 18.3265
2353 | 25.9448 | 22.5343 | 20.0044 | 15.9049 | 11.7156 | 9.8885 | 10.785 | 14.3801 | 18.2187 | 21.1759 | 22.8235 | 26.616 | 18.3326
2354 | 23.6969 | 20.3318 | 18.1269 | 15.0144 | 11.0053 | 9.7677 | 10.7595 | 14.1529 | 18.3245 | 20.967 | 21.1251 | 24.6089 | 17.3234
2355 | 25.6949 | 22.5122 | 20.1229 | 16.1338 | 11.8753 | 10.1135 | 11.0835 | 14.5998 | 18.498 | 21.3734 | 22.984 | 26.1634 | 18.4296
2357 | 26.3182 | 23.2726 | 20.7471 | 16.2971 | 12.2285 | 10.3759 | 11.3883 | 14.6343 | 18.7186 | 21.8772 | 24.0647 | 27.622 | 18.962
2358 | 25.9214 | 22.2671 | 20.1356 | 16.195 | 11.9881 | 10.3068 | 11.2309 | 14.6844 | 18.6897 | 21.5977 | 23.1606 | 26.2445 | 18.5352
2359 | 26.0502 | 22.6804 | 20.3106 | 16.5297 | 12.5098 | 10.7751 | 11.6522 | 15.1208 | 19.0729 | 21.7445 | 23.355 | 26.4457 | 18.8539
2360 | 26.1151 | 22.8072 | 20.7524 | 16.7648 | 12.8546 | 11.0188 | 12.0162 | 15.5341 | 19.4124 | 22.2257 | 23.6249 | 26.6529 | 19.1483
2361 | 26.3686 | 22.9469 | 21.3525 | 17.2149 | 13.399 | 11.3853 | 12.4043 | 16.1004 | 19.7116 | 22.3772 | 24.4205 | 27.0989 | 19.565
2365 | 24.7595 | 21.2618 | 19.1776 | 15.9554 | 11.9966 | 10.3827 | 11.4535 | 14.91 | 19.0664 | 21.6788 | 22.0765 | 25.2725 | 18.1659
2369 | 25.2927 | 21.9656 | 19.9311 | 16.2949 | 12.372 | 10.5099 | 11.4604 | 14.8161 | 18.6383 | 21.5045 | 22.5948 | 25.4408 | 18.4018
2370 | 23.0654 | 19.775 | 18.1516 | 15.7707 | 12.0906 | 10.6533 | 11.7427 | 15.2095 | 19.0373 | 21.0051 | 21.5394 | 24.1138 | 17.6795
2371 | 25.3892 | 21.75 | 20.0116 | 16.4625 | 12.7369 | 10.9516 | 11.8729 | 15.4228 | 19.0319 | 21.8584 | 23.1988 | 26.233 | 18.7433
2372 | 24.6991 | 21.3033 | 19.5671 | 16.6162 | 12.6996 | 10.9882 | 12.0048 | 15.5334 | 19.3393 | 21.4219 | 22.7447 | 25.5376 | 18.5379
2380 | 27.1281 | 23.8975 | 21.2901 | 16.693 | 12.6763 | 10.6818 | 11.6285 | 15.195 | 19.0627 | 22.3804 | 24.7561 | 27.8144 | 19.4337
2381 | 26.8389 | 23.8964 | 21.1137 | 16.5203 | 12.2677 | 10.4419 | 11.3359 | 14.9107 | 18.7726 | 22.1294 | 24.2724 | 27.7121 | 19.1843
2382 | 27.1613 | 23.8713 | 21.5149 | 16.8769 | 12.7795 | 10.779 | 11.8347 | 15.2686 | 19.1188 | 22.5153 | 24.7801 | 27.8771 | 19.5315
2386 | 26.9582 | 23.8696 | 21.939 | 17.3769 | 13.2562 | 11.1867 | 12.1354 | 15.6056 | 19.7157 | 23.1119 | 24.9773 | 28.0897 | 19.8518
2388 | 27.0561 | 23.8794 | 21.7108 | 17.1278 | 13.1982 | 11.1255 | 12.1315 | 15.4463 | 19.3708 | 22.6341 | 24.815 | 28.1691 | 19.722
2390 | 26.6247 | 23.3365 | 21.2857 | 16.8642 | 12.7396 | 10.7533 | 11.8626 | 15.2905 | 19.3826 | 22.3642 | 24.5123 | 27.5001 | 19.3764
2395 | 26.4087 | 23.2528 | 20.7013 | 15.9906 | 11.9441 | 10.0676 | 11.0093 | 14.3657 | 18.4236 | 21.9559 | 24.257 | 27.7623 | 18.8449
2396 | 26.5773 | 23.2853 | 21.1947 | 16.5293 | 12.3559 | 10.3828 | 11.4972 | 14.8558 | 19.0415 | 22.1804 | 24.3792 | 27.6439 | 19.1603
2397 | 26.8606 | 23.8469 | 21.71 | 17.2846 | 13.159 | 11.1415 | 12.2168 | 15.6728 | 19.7055 | 22.6209 | 24.8278 | 27.9007 | 19.7456
2399 | 26.6869 | 23.6057 | 21.6726 | 17.243 | 13.1997 | 11.1941 | 12.24 | 15.644 | 19.7645 | 22.5951 | 24.5336 | 27.4205 | 19.65
2400 | 26.9204 | 24.1547 | 22.2021 | 17.5067 | 13.5079 | 11.5381 | 12.5438 | 16.2297 | 20.2843 | 22.844 | 25.0095 | 27.8517 | 20.0494
2401 | 26.8911 | 23.6503 | 21.5769 | 17.3145 | 13.2708 | 11.25 | 12.2278 | 15.8845 | 19.9812 | 22.5411 | 24.5798 | 27.532 | 19.725
2402 | 26.5171 | 23.2358 | 21.3413 | 17.3296 | 13.3995 | 11.3454 | 12.3253 | 15.8753 | 20.0066 | 22.4048 | 24.4948 | 27.2235 | 19.6249
2403 | 26.3909 | 23.1163 | 20.9968 | 17.0751 | 13.0039 | 11.0176 | 12.0658 | 15.5947 | 19.6296 | 22.2314 | 24.1025 | 26.8843 | 19.3424
2404 | 26.4045 | 23.3098 | 21.2585 | 16.9662 | 12.8662 | 10.9865 | 12.0457 | 15.4915 | 19.5934 | 22.2091 | 24.1003 | 27.0378 | 19.3558
2405 | 27.121 | 24.0245 | 22.2085 | 17.7062 | 13.7673 | 11.9257 | 12.8816 | 16.6244 | 20.5687 | 22.8532 | 25.2544 | 27.8731 | 20.234
2406 | 27.0844 | 24.0411 | 22.3213 | 17.7092 | 13.8006 | 11.7611 | 12.8955 | 16.5683 | 20.5095 | 23.0602 | 25.2093 | 28.0598 | 20.2517
2408 | 26.9371 | 23.597 | 21.9323 | 17.7552 | 13.7813 | 11.7814 | 12.6024 | 16.1556 | 20.227 | 22.726 | 25.145 | 27.7045 | 20.0287
2409 | 27.0948 | 23.9163 | 22.0782 | 17.9121 | 13.7968 | 11.9287 | 12.7895 | 16.5186 | 20.4663 | 22.8754 | 25.2963 | 27.7766 | 20.2041
2410 | 26.3445 | 23.181 | 21.4646 | 17.6829 | 13.5376 | 11.616 | 12.5909 | 16.2124 | 20.0452 | 22.2242 | 24.4155 | 27.0977 | 19.701
2415 | 22.1536 | 19.6927 | 16.6887 | 14.3833 | 10.5081 | 9.5789 | 10.3698 | 13.9824 | 17.3188 | 19.7104 | 20.4171 | 22.5242 | 16.444
2420 | 22.5473 | 20.1978 | 16.7469 | 14.3216 | 10.2755 | 9.2818 | 10.0247 | 13.9718 | 17.2741 | 20.0037 | 20.8089 | 23.2232 | 16.5564
2421 | 23.1345 | 20.2335 | 16.9819 | 14.4266 | 10.4686 | 9.4494 | 10.1208 | 14.0623 | 17.5219 | 20.3895 | 21.3485 | 23.8043 | 16.8285
2422 | 22.1965 | 19.2624 | 16.4996 | 14.4617 | 10.5573 | 9.5935 | 10.4992 | 14.0011 | 17.424 | 19.8774 | 20.1366 | 22.5935 | 16.4252
2423 | 22.5112 | 20.2337 | 17.1011 | 14.5479 | 10.5204 | 9.4349 | 10.3143 | 14.0114 | 17.3189 | 19.8172 | 20.852 | 22.6509 | 16.6095
2424 | 22.2068 | 19.6552 | 16.8925 | 14.5869 | 10.6342 | 9.7167 | 10.5963 | 14.1561 | 17.8941 | 19.9806 | 20.4204 | 23.0499 | 16.6491
2425 | 22.4537 | 19.9284 | 16.7606 | 14.302 | 10.0873 | 9.2224 | 9.9528 | 13.7549 | 17.1621 | 19.7092 | 20.7113 | 22.7152 | 16.3967
2426 | 22.7101 | 20.6681 | 17.6517 | 14.8859 | 10.937 | 9.7841 | 10.6717 | 14.3809 | 17.9788 | 20.1338 | 20.883 | 22.9313 | 16.968
2427 | 23.7257 | 21.725 | 18.5451 | 15.3163 | 10.8021 | 9.6166 | 10.577 | 14.4347 | 18.5757 | 20.5213 | 21.8102 | 24.1315 | 17.4818
2428 | 23.565 | 21.1923 | 18.1953 | 15.1807 | 10.6616 | 9.4853 | 10.3566 | 14.2047 | 17.9831 | 20.3078 | 21.5293 | 23.6418 | 17.192
2429 | 21.9716 | 19.3261 | 16.4059 | 14.6437 | 10.6135 | 9.7986 | 10.6187 | 14.0719 | 17.6169 | 19.597 | 20.355 | 22.324 | 16.4452
2430 | 22.8101 | 20.6192 | 17.4165 | 14.7673 | 10.8606 | 9.7516 | 10.5482 | 14.1852 | 17.8475 | 19.9904 | 20.958 | 23.3425 | 16.9248
2431 | 24.7189 | 22.0215 | 19.3769 | 16.2334 | 11.5458 | 10.6385 | 11.4104 | 15.201 | 19.2225 | 21.5242 | 22.4415 | 24.7548 | 18.2574
2439 | 22.5597 | 20.2301 | 17.5535 | 15.2014 | 11.1877 | 10.1789 | 10.9752 | 14.4254 | 18.2141 | 20.1255 | 20.7786 | 22.9177 | 17.029
2440 | 22.6143 | 19.6419 | 17.6432 | 15.3874 | 11.5934 | 10.56 | 11.4355 | 14.9184 | 18.5911 | 20.631 | 21.1654 | 23.3368 | 17.2932
2441 | 22.7073 | 19.9921 | 17.5306 | 15.3192 | 11.4106 | 10.3511 | 11.2013 | 14.5796 | 18.2537 | 20.1411 | 20.675 | 22.5495 | 17.0593
2443 | 23.2675 | 21.4967 | 18.2129 | 15.079 | 10.8239 | 9.7542 | 10.6451 | 14.5055 | 18.4748 | 20.3723 | 21.246 | 23.5214 | 17.2833
2444 | 24.0874 | 21.5768 | 18.8359 | 15.8991 | 11.2053 | 10.1626 | 11.0401 | 14.7884 | 18.8867 | 21.1138 | 21.9043 | 23.912 | 17.7844
2445 | 24.2284 | 21.9782 | 19.0235 | 15.7411 | 11.1546 | 10.0196 | 10.842 | 14.7055 | 18.9156 | 20.9075 | 22.1099 | 24.3649 | 17.8326
2446 | 21.7 | 19.138 | 16.8447 | 14.8084 | 10.8562 | 9.9622 | 10.7804 | 14.1466 | 17.8409 | 19.7354 | 20.0259 | 21.9921 | 16.4859
2447 | 22.9894 | 20.7525 | 17.9776 | 15.5858 | 11.5926 | 10.6054 | 11.3391 | 14.9783 | 18.8328 | 20.5504 | 21.1061 | 23.3178 | 17.469
2448 | 23.5122 | 20.9762 | 18.319 | 15.6933 | 11.5617 | 10.5273 | 11.4327 | 15.162 | 19.1929 | 20.865 | 21.1411 | 23.5912 | 17.6645
2449 | 22.2277 | 19.8868 | 17.2311 | 15.3706 | 11.5185 | 10.6017 | 11.2686 | 14.8736 | 18.5941 | 20.1529 | 20.4442 | 22.6698 | 17.07
2450 | 23.1388 | 20.4335 | 18.1031 | 15.9909 | 11.9998 | 10.9134 | 11.8305 | 15.3709 | 18.9909 | 20.7805 | 21.293 | 23.1923 | 17.6698
2452 | 23.8309 | 21.2355 | 18.7652 | 16.0712 | 11.6004 | 10.5318 | 11.558 | 15.3496 | 19.505 | 21.1347 | 21.6316 | 23.8957 | 17.9258
2453 | 22.3753 | 19.6062 | 17.2895 | 15.5974 | 11.6971 | 10.661 | 11.8246 | 15.0003 | 18.6227 | 20.2443 | 20.4407 | 22.6449 | 17.167
2454 | 21.6875 | 19.3848 | 16.744 | 15.1247 | 11.39 | 10.2921 | 11.2692 | 14.644 | 18.6906 | 20.2001 | 20.3391 | 22.1182 | 16.8237
2455 | 23.507 | 21.0451 | 18.4612 | 15.6719 | 11.5194 | 10.4777 | 11.3729 | 15.1873 | 19.2414 | 20.8867 | 21.1542 | 23.6612 | 17.6822
2456 | 24.132 | 21.3288 | 19.1202 | 16.3489 | 12.0028 | 10.8063 | 11.9229 | 15.6633 | 19.5933 | 21.3974 | 22.248 | 24.3941 | 18.2465
2460 | 23.5494 | 20.6876 | 19.0396 | 16.3461 | 12.5073 | 11.1419 | 12.2622 | 15.7486 | 19.4065 | 21.1274 | 22.2519 | 24.218 | 18.1905
2462 | 23.9954 | 21.3933 | 19.1465 | 16.1937 | 12.2044 | 10.9481 | 12.0451 | 15.6885 | 19.6062 | 21.5937 | 22.7442 | 24.6486 | 18.3506
2463 | 24.2428 | 21.5272 | 19.1699 | 15.9439 | 12.1321 | 10.874 | 12.1632 | 15.7997 | 19.7093 | 21.4488 | 22.8865 | 24.9167 | 18.4012
2464 | 24.8272 | 21.9713 | 19.7438 | 16.2245 | 12.0859 | 10.7111 | 12.0077 | 15.758 | 19.9934 | 21.8717 | 23.2029 | 25.3664 | 18.647
2465 | 24.1499 | 21.503 | 19.0969 | 16.0487 | 12.1228 | 10.9631 | 12.2053 | 15.7308 | 19.6494 | 21.3723 | 22.7487 | 24.7501 | 18.3618
2466 | 25.0956 | 22.0862 | 19.9051 | 16.4816 | 12.1968 | 10.7963 | 12.2231 | 15.861 | 20.0376 | 21.9592 | 23.5771 | 25.7274 | 18.8289
2469 | 22.8377 | 20.1708 | 18.4442 | 15.7566 | 12.368 | 10.9386 | 12.3111 | 15.6777 | 19.3413 | 20.8993 | 22.2772 | 23.8359 | 17.9049
2470 | 23.4095 | 20.684 | 18.8406 | 16.0384 | 12.3697 | 10.9329 | 12.2473 | 15.6727 | 19.4956 | 21.2949 | 22.7947 | 24.4399 | 18.185
2471 | 24.0645 | 21.2954 | 18.969 | 15.8987 | 12.3411 | 10.9813 | 12.1841 | 15.5558 | 19.4708 | 21.4781 | 23.0514 | 24.723 | 18.3344
2472 | 24.2319 | 21.4155 | 19.1954 | 15.8003 | 12.2586 | 10.9104 | 12.279 | 15.7054 | 19.6785 | 21.551 | 22.9956 | 24.8956 | 18.4098
2473 | 24.5576 | 21.7912 | 19.5895 | 16.0591 | 12.0057 | 10.6136 | 12.1711 | 15.8041 | 19.9972 | 21.7644 | 23.2008 | 25.3741 | 18.5774
2474 | 22.7774 | 19.6769 | 18.2069 | 15.5627 | 12.1548 | 10.8834 | 12.3252 | 15.5538 | 19.5243 | 20.8992 | 22.3466 | 23.8989 | 17.8175
2475 | 22.8412 | 19.4277 | 17.8986 | 15.5806 | 12.1664 | 10.9068 | 12.2144 | 15.5113 | 19.5013 | 21.293 | 22.4968 | 23.8032 | 17.8034
2476 | 24.06 | 20.8803 | 19.2471 | 16.4245 | 12.814 | 11.4021 | 12.6767 | 16.091 | 19.9183 | 21.6983 | 23.4014 | 25.0844 | 18.6415
2477 | 23.8328 | 21.3107 | 18.9207 | 15.5243 | 11.9802 | 10.7629 | 12.1152 | 15.5124 | 19.6235 | 21.427 | 22.7931 | 24.5526 | 18.1963
2478 | 24.1247 | 21.5943 | 19.2398 | 15.7589 | 11.8777 | 10.5769 | 12.0673 | 15.6321 | 19.8422 | 21.3901 | 23.0292 | 24.7655 | 18.3249
2479 | 23.1013 | 20.7188 | 18.8603 | 15.611 | 12.0748 | 10.871 | 12.2018 | 15.409 | 19.3925 | 21.0595 | 22.3731 | 24.0956 | 17.9807
2480 | 22.9006 | 20.1765 | 18.3682 | 15.6683 | 12.0422 | 10.789 | 12.0633 | 15.4015 | 19.0984 | 20.9398 | 22.2257 | 23.8891 | 17.7969
2481 | 24.3397 | 21.555 | 19.8144 | 16.3167 | 12.1575 | 10.8863 | 12.4824 | 15.6969 | 20.0008 | 21.6038 | 23.4857 | 25.1308 | 18.6225
2482 | 22.3198 | 19.9444 | 18.46 | 15.6256 | 12.3098 | 11.0524 | 12.4286 | 15.3057 | 19.3504 | 20.5999 | 21.5948 | 23.1371 | 17.6774
2483 | 23.5593 | 20.8138 | 19.3333 | 16.0424 | 12.3255 | 11.0488 | 12.6755 | 15.6809 | 19.9789 | 21.1495 | 22.4369 | 24.0872 | 18.261
2484 | 22.1066 | 19.1907 | 18.0411 | 15.4958 | 12.3384 | 10.9138 | 12.2759 | 15.1028 | 18.961 | 20.3839 | 21.6434 | 22.8773 | 17.4442
2485 | 24.6202 | 21.6072 | 20.2049 | 16.5725 | 12.7288 | 11.3649 | 12.9762 | 16.123 | 20.2971 | 21.318 | 23.0116 | 24.947 | 18.8143
2486 | 23.9565 | 21.207 | 19.8911 | 16.3659 | 12.7234 | 11.391 | 12.9202 | 15.9275 | 20.1323 | 21.1271 | 22.6719 | 24.4787 | 18.5661
2487 | 24.5403 | 21.7837 | 20.1337 | 16.6181 | 12.4997 | 11.1376 | 12.8512 | 16.1964 | 20.4139 | 21.5045 | 23.1933 | 25.0202 | 18.8244
2488 | 24.33 | 21.6432 | 20.0941 | 16.5514 | 12.3968 | 11.0685 | 12.7693 | 16.1521 | 20.4233 | 21.6024 | 23.1617 | 24.8401 | 18.7527
2489 | 24.2913 | 21.6046 | 20.0296 | 16.5111 | 12.3245 | 11.0644 | 12.7008 | 15.9613 | 20.3075 | 21.5338 | 23.0458 | 24.7607 | 18.6779
2490 | 23.4089 | 20.7542 | 19.4958 | 16.0289 | 12.6686 | 11.356 | 12.8243 | 15.7541 | 19.9783 | 21.0748 | 22.4493 | 24.0919 | 18.3238
2500 | 22.6201 | 20.2259 | 17.0734 | 13.8583 | 9.8552 | 8.6856 | 9.8486 | 13.4786 | 17.2298 | 19.7235 | 20.0906 | 22.9929 | 16.3069
2502 | 23.0773 | 20.7015 | 17.5194 | 14.1072 | 9.896 | 8.4817 | 9.7107 | 13.303 | 17.2435 | 19.8695 | 20.6998 | 23.4517 | 16.5051
2505 | 22.684 | 20.4318 | 17.3099 | 13.9615 | 9.8326 | 8.5804 | 9.7758 | 13.4052 | 17.2344 | 19.7322 | 20.2842 | 23.1093 | 16.3618
2506 | 22.2412 | 20.0445 | 16.9788 | 13.7293 | 9.7383 | 8.531 | 9.7479 | 13.3597 | 17.086 | 19.5225 | 19.895 | 22.7315 | 16.1338
2508 | 23.1306 | 20.3242 | 17.2951 | 13.836 | 9.9685 | 8.9178 | 10.001 | 13.4782 | 17.0888 | 19.9997 | 21.2328 | 23.627 | 16.575
2515 | 22.9628 | 20.4871 | 17.2136 | 13.9489 | 9.8084 | 8.7425 | 9.9905 | 13.5156 | 17.2078 | 20.0298 | 20.6797 | 23.4356 | 16.5019
2516 | 22.7112 | 20.1063 | 16.914 | 13.7854 | 9.776 | 8.7246 | 9.9462 | 13.5151 | 17.1698 | 19.8155 | 20.2872 | 23.1474 | 16.3249
2517 | 22.7112 | 20.1063 | 16.914 | 13.7854 | 9.776 | 8.7246 | 9.9462 | 13.5151 | 17.1698 | 19.8155 | 20.2872 | 23.1474 | 16.3249
2518 | 22.7112 | 20.1063 | 16.914 | 13.7854 | 9.776 | 8.7246 | 9.9462 | 13.5151 | 17.1698 | 19.8155 | 20.2872 | 23.1474 | 16.3249
2519 | 22.6201 | 20.2259 | 17.0734 | 13.8583 | 9.8552 | 8.6856 | 9.8486 | 13.4786 | 17.2298 | 19.7235 | 20.0906 | 22.9929 | 16.3069
2525 | 22.1359 | 19.7836 | 16.6214 | 13.5951 | 9.8192 | 8.6912 | 9.8643 | 13.3529 | 16.9581 | 19.4678 | 19.6923 | 22.7022 | 16.057
2526 | 22.0753 | 19.4773 | 16.3605 | 13.4751 | 9.8219 | 8.7416 | 9.873 | 13.2795 | 16.697 | 19.2258 | 19.7021 | 22.6044 | 15.9445
2527 | 21.1988 | 18.656 | 15.6831 | 13.2517 | 9.7741 | 8.6642 | 9.7177 | 12.9583 | 16.0369 | 19.0273 | 19.1899 | 21.5802 | 15.4782
2528 | 22.5468 | 20.163 | 17.392 | 13.8057 | 9.7784 | 8.3744 | 9.5813 | 13.3397 | 17.1334 | 19.5364 | 20.3448 | 23.0331 | 16.2524
2529 | 23.1369 | 20.3594 | 17.5861 | 13.8664 | 9.8723 | 8.4207 | 9.615 | 13.2123 | 17.0995 | 19.4866 | 20.6067 | 23.2664 | 16.3773
2530 | 21.859 | 19.1239 | 16.2259 | 13.4552 | 9.7694 | 8.7341 | 9.7791 | 13.157 | 16.4087 | 19.1946 | 19.3754 | 22.2592 | 15.7785
2533 | 21.5593 | 19.304 | 16.2233 | 13.2385 | 9.7474 | 8.5797 | 9.6569 | 13.1983 | 16.5147 | 19.1045 | 19.4336 | 21.823 | 15.6986
2534 | 22.1084 | 20.0213 | 16.73 | 13.4595 | 9.5053 | 8.2104 | 9.4627 | 13.118 | 16.8647 | 19.4959 | 19.8054 | 22.5266 | 15.9423
2535 | 21.4469 | 19.0895 | 15.9862 | 12.7004 | 9.3535 | 8.2901 | 9.3205 | 12.8826 | 16.3493 | 19.1156 | 19.4549 | 22.0459 | 15.503
2536 | 20.6698 | 19.0471 | 16.3186 | 13.0635 | 9.4045 | 8.1078 | 9.2392 | 12.7451 | 16.3551 | 18.9597 | 20.0619 | 21.6498 | 15.4685
2537 | 21.6264 | 20.0712 | 17.1312 | 13.3172 | 9.5214 | 8.0498 | 9.2896 | 12.7686 | 16.5066 | 19.4407 | 20.915 | 22.3847 | 15.9185
2538 | 21.0599 | 18.9018 | 16.1498 | 12.9995 | 9.3986 | 8.1742 | 9.2596 | 12.681 | 16.1337 | 19.2791 | 19.9496 | 21.9186 | 15.4921
2539 | 21.9415 | 19.7504 | 16.832 | 13.4414 | 9.3508 | 8.1673 | 9.3691 | 12.8728 | 16.5319 | 19.2436 | 20.1674 | 22.2434 | 15.826
2540 | 21.9373 | 19.4294 | 16.5913 | 13.3681 | 9.6734 | 8.379 | 9.4859 | 13.0522 | 16.5536 | 19.5942 | 20.4015 | 22.8975 | 15.9469
2541 | 21.5354 | 19.0682 | 15.9807 | 12.9408 | 9.4708 | 8.2956 | 9.3104 | 12.9662 | 16.3491 | 19.4384 | 19.9502 | 22.7048 | 15.6676
2545 | 20.8899 | 19.0953 | 16.3465 | 13.02 | 9.3613 | 7.9642 | 9.1267 | 12.5533 | 15.8101 | 19.0719 | 20.3968 | 21.8118 | 15.454
2546 | 21.7179 | 20.1972 | 16.9329 | 13.082 | 9.2458 | 7.8428 | 9.1242 | 12.511 | 16.1756 | 19.257 | 21.1675 | 22.2652 | 15.7933
2548 | 22.5017 | 20.7712 | 17.8318 | 13.319 | 9.0657 | 7.3421 | 8.6451 | 12.1334 | 15.9375 | 19.3207 | 21.7726 | 23.2701 | 15.9926
2549 | 22.1147 | 20.5241 | 17.3464 | 13.0161 | 8.9344 | 7.3258 | 8.5184 | 12.0129 | 15.6064 | 19.1612 | 21.1296 | 22.8413 | 15.711
2550 | 21.5633 | 19.8647 | 16.5759 | 12.8226 | 9.1007 | 7.5625 | 8.7027 | 12.0584 | 15.2012 | 18.8051 | 20.9273 | 22.4553 | 15.47
2551 | 21.6132 | 19.8607 | 16.491 | 12.5564 | 8.6408 | 7.1045 | 8.2167 | 11.6607 | 14.9355 | 18.3249 | 20.6702 | 22.524 | 15.2165
2555 | 22.6372 | 19.7671 | 16.7082 | 14.0585 | 10.29 | 9.0346 | 10.142 | 13.6338 | 16.9028 | 19.9006 | 20.8497 | 23.2677 | 16.4327
2556 | 22.688 | 19.8997 | 16.7401 | 14.1009 | 10.2837 | 9.0663 | 10.114 | 13.5816 | 16.9388 | 20.0167 | 20.9158 | 23.3816 | 16.4773
2557 | 22.688 | 19.8997 | 16.7401 | 14.1009 | 10.2837 | 9.0663 | 10.114 | 13.5816 | 16.9388 | 20.0167 | 20.9158 | 23.3816 | 16.4773
2558 | 22.8128 | 20.1344 | 16.9098 | 14.0073 | 10.1549 | 9.0357 | 10.0281 | 13.5167 | 17.0309 | 20.0386 | 20.9995 | 23.481 | 16.5125
2559 | 22.8128 | 20.1344 | 16.9098 | 14.0073 | 10.1549 | 9.0357 | 10.0281 | 13.5167 | 17.0309 | 20.0386 | 20.9995 | 23.481 | 16.5125
2560 | 22.7706 | 20.1031 | 17.0491 | 13.9292 | 10.0699 | 8.9837 | 10.0081 | 13.5164 | 16.9775 | 20.0221 | 21.0619 | 23.4621 | 16.4962
2563 | 22.796 | 20.0783 | 16.9118 | 13.9267 | 10.1824 | 8.9832 | 9.9873 | 13.5634 | 17.0051 | 20.0874 | 21.0382 | 23.3756 | 16.4946
2564 | 22.8808 | 20.1878 | 17.0633 | 13.9519 | 10.1015 | 9.041 | 10.0525 | 13.5372 | 16.9696 | 20.0476 | 21.0319 | 23.4861 | 16.5293
2565 | 22.9192 | 20.1606 | 16.9878 | 13.9677 | 10.1677 | 9.0124 | 10.0215 | 13.5845 | 17.0262 | 20.0456 | 21.034 | 23.5046 | 16.536
2566 | 22.9192 | 20.1606 | 16.9878 | 13.9677 | 10.1677 | 9.0124 | 10.0215 | 13.5845 | 17.0262 | 20.0456 | 21.034 | 23.5046 | 16.536
2567 | 22.7394 | 19.9725 | 16.8357 | 14.0896 | 10.2044 | 9.0121 | 10.0337 | 13.5896 | 16.9723 | 19.9973 | 20.9666 | 23.3582 | 16.4809
2568 | 22.5934 | 19.7475 | 16.8373 | 13.8855 | 10.2069 | 8.9988 | 10.0162 | 13.5661 | 16.982 | 19.9969 | 20.8181 | 23.3988 | 16.4206
2569 | 22.7284 | 20.0055 | 16.9098 | 13.8302 | 10.1562 | 9.0059 | 9.9947 | 13.5218 | 16.9821 | 20.0826 | 20.9832 | 23.4465 | 16.4706
2570 | 21.9037 | 19.2137 | 16.4273 | 13.8169 | 10.0203 | 9.0842 | 10.0818 | 13.5204 | 16.6362 | 19.6876 | 20.3195 | 22.7748 | 16.1239
2571 | 22.5313 | 19.5746 | 16.7679 | 13.7804 | 10.1109 | 8.9494 | 10.0142 | 13.5978 | 16.9224 | 19.9642 | 20.7014 | 23.1653 | 16.34
2572 | 21.9181 | 19.2953 | 16.386 | 13.6736 | 10.0491 | 8.869 | 10.0023 | 13.4703 | 16.6391 | 19.7616 | 20.3274 | 22.9198 | 16.1093
2573 | 22.3143 | 19.4644 | 16.7512 | 13.6361 | 10.0402 | 8.8941 | 10.0087 | 13.6024 | 16.8531 | 19.8369 | 20.6281 | 22.8863 | 16.243
2574 | 22.0798 | 19.1991 | 16.3228 | 13.7487 | 9.8996 | 8.8185 | 9.9062 | 13.2879 | 16.6633 | 19.4526 | 20.046 | 22.7794 | 16.017
2575 | 22.1701 | 19.3806 | 16.3549 | 13.693 | 9.7431 | 8.5854 | 9.5832 | 13.1993 | 16.8507 | 19.7649 | 20.3886 | 23.4133 | 16.0939
2576 | 21.6739 | 18.7351 | 15.9766 | 13.6044 | 9.7716 | 8.7132 | 9.8097 | 13.2234 | 16.5845 | 19.3622 | 19.8658 | 22.2927 | 15.8011
2577 | 21.9439 | 19.0571 | 15.8506 | 13.2584 | 9.4325 | 8.3773 | 9.4894 | 13.0026 | 16.5478 | 19.6929 | 20.3763 | 23.1338 | 15.8469
2578 | 22.4554 | 19.505 | 16.3009 | 13.3001 | 9.5908 | 8.3574 | 9.3859 | 13.1284 | 16.7193 | 19.8283 | 20.9531 | 23.9284 | 16.1211
2579 | 23.4088 | 20.5428 | 17.2544 | 13.6617 | 9.8683 | 8.3664 | 9.2724 | 12.9788 | 16.7847 | 20.124 | 21.8778 | 25.0319 | 16.5977
2580 | 24.3351 | 21.1685 | 17.924 | 13.8215 | 9.7898 | 8.0795 | 9.0312 | 12.7281 | 16.7599 | 20.4071 | 22.607 | 26.2176 | 16.9058
2581 | 26.3398 | 23.0049 | 19.6977 | 14.4106 | 9.9187 | 7.723 | 8.5195 | 12.1283 | 16.0258 | 20.3666 | 23.7696 | 27.7658 | 17.4725
2582 | 26.8391 | 23.5922 | 19.9333 | 14.4361 | 10.0539 | 7.6733 | 8.5731 | 12.2785 | 16.1904 | 20.8862 | 24.1866 | 28.007 | 17.7208
2583 | 26.2109 | 22.8641 | 19.735 | 14.6608 | 9.9751 | 7.8607 | 8.6882 | 12.3624 | 16.0872 | 20.2685 | 23.0864 | 27.4708 | 17.4392
2584 | 27.3945 | 24.0083 | 20.6439 | 14.7796 | 10.1592 | 7.7732 | 8.7203 | 12.093 | 15.9261 | 20.6384 | 24.7245 | 28.2503 | 17.9259
2585 | 27.4451 | 24.273 | 20.8345 | 14.9433 | 10.3274 | 7.9598 | 8.9061 | 12.2031 | 15.9099 | 20.7888 | 24.6124 | 28.1593 | 18.0302
2586 | 27.156 | 23.9504 | 20.5713 | 14.9549 | 10.2863 | 8.0564 | 8.9362 | 12.4751 | 16.2986 | 20.963 | 24.2143 | 28.2035 | 18.0055
2587 | 27.5301 | 24.3241 | 20.8895 | 15.0623 | 10.4345 | 8.0803 | 8.9584 | 12.293 | 16.117 | 20.8657 | 24.8973 | 28.4269 | 18.1566
2588 | 27.5933 | 24.4538 | 21.2854 | 15.0537 | 10.3408 | 7.925 | 8.8763 | 12.1588 | 16.0335 | 20.8585 | 24.8007 | 28.1696 | 18.1291
2590 | 27.5455 | 24.0847 | 21.2034 | 14.9754 | 10.1701 | 7.8434 | 8.8451 | 12.1519 | 16.0209 | 20.9002 | 24.7715 | 28.3589 | 18.0726
2594 | 27.7478 | 24.214 | 21.1411 | 15.2721 | 10.5181 | 8.2585 | 9.0791 | 12.3228 | 16.2429 | 20.9818 | 24.6083 | 28.3307 | 18.2264
2600 | 25.5356 | 22.8237 | 19.364 | 14.1234 | 10.0965 | 7.9782 | 9.0772 | 12.7202 | 16.5863 | 20.7931 | 23.9125 | 27.3154 | 17.5272
2601 | 25.5356 | 22.8237 | 19.364 | 14.1234 | 10.0965 | 7.9782 | 9.0772 | 12.7202 | 16.5863 | 20.7931 | 23.9125 | 27.3154 | 17.5272
2602 | 25.7301 | 22.95 | 19.3586 | 14.1869 | 10.1073 | 8.1121 | 9.0742 | 12.7283 | 16.6906 | 20.7656 | 23.8494 | 27.4962 | 17.5874
2603 | 25.3987 | 22.663 | 19.2696 | 14.1462 | 10.0622 | 8.0199 | 9.0608 | 12.6611 | 16.4753 | 20.631 | 23.6673 | 27.2642 | 17.4433
2604 | 25.3343 | 22.6514 | 19.2327 | 14.0228 | 10.0439 | 8.0456 | 9.1198 | 12.7158 | 16.5454 | 20.597 | 23.6857 | 27.2778 | 17.4394
2605 | 25.3987 | 22.663 | 19.2696 | 14.1462 | 10.0622 | 8.0199 | 9.0608 | 12.6611 | 16.4753 | 20.631 | 23.6673 | 27.2642 | 17.4433
2606 | 25.3987 | 22.663 | 19.2696 | 14.1462 | 10.0622 | 8.0199 | 9.0608 | 12.6611 | 16.4753 | 20.631 | 23.6673 | 27.2642 | 17.4433
2607 | 25.3987 | 22.663 | 19.2696 | 14.1462 | 10.0622 | 8.0199 | 9.0608 | 12.6611 | 16.4753 | 20.631 | 23.6673 | 27.2642 | 17.4433
2609 | 25.59 | 22.7374 | 19.271 | 14.1784 | 9.9636 | 7.9978 | 9.0356 | 12.689 | 16.603 | 20.7442 | 23.721 | 27.3418 | 17.4894
2611 | 25.1872 | 22.6668 | 19.0746 | 14.0561 | 9.847 | 7.865 | 8.9797 | 12.5866 | 16.3705 | 20.6299 | 23.5419 | 27.1282 | 17.3278
2612 | 25.4665 | 22.8442 | 19.4128 | 14.0523 | 10.0829 | 8.0625 | 9.0882 | 12.7573 | 16.6193 | 20.671 | 23.7994 | 27.3389 | 17.5163
2614 | 25.7707 | 23.0377 | 19.4861 | 14.1056 | 10.0828 | 7.9289 | 8.9867 | 12.6633 | 16.6594 | 20.9005 | 23.8788 | 27.5191 | 17.585
2615 | 25.9188 | 23.1425 | 19.5098 | 14.1204 | 9.9867 | 7.9172 | 8.9939 | 12.5739 | 16.5589 | 20.7552 | 23.9294 | 27.4528 | 17.5716
2617 | 25.7789 | 22.9775 | 19.4362 | 14.1546 | 10.151 | 8.0094 | 9.0488 | 12.7198 | 16.6084 | 20.8982 | 24.0268 | 27.5458 | 17.613
2618 | 26.2606 | 23.2638 | 19.654 | 14.4174 | 9.9954 | 7.8842 | 8.8333 | 12.5304 | 16.5799 | 20.792 | 23.8351 | 27.6066 | 17.6377
2619 | 25.3455 | 22.6031 | 19.1529 | 14.0756 | 9.9413 | 8.0304 | 9.1536 | 12.8088 | 16.6461 | 20.5974 | 23.5308 | 27.1265 | 17.4177
2620 | 24.5694 | 21.9716 | 18.7892 | 13.7615 | 9.7017 | 7.8299 | 9.0893 | 12.7396 | 16.4517 | 20.4107 | 23.0972 | 26.4746 | 17.0739
2621 | 25.0294 | 22.1728 | 18.6381 | 13.9078 | 9.8414 | 8.0636 | 9.1187 | 12.7976 | 16.5289 | 20.5246 | 23.3047 | 26.7516 | 17.2233
2622 | 22.3875 | 20.0798 | 16.8846 | 13.3986 | 9.6042 | 8.0751 | 9.225 | 12.7337 | 16.4084 | 19.7987 | 21.5419 | 24.4071 | 16.2121
2623 | 24.2438 | 21.4116 | 18.1877 | 13.7372 | 9.6423 | 7.9639 | 9.0419 | 12.6712 | 16.4445 | 20.2299 | 22.8044 | 26.0112 | 16.8658
2625 | 24.1832 | 22.0459 | 18.1255 | 12.5288 | 7.3806 | 4.4671 | 4.5676 | 8.0055 | 12.1753 | 17.9237 | 22.2113 | 26.2357 | 14.9875
2626 | 24.4093 | 21.7426 | 18.7028 | 13.6089 | 9.4307 | 7.7496 | 9.0404 | 12.6665 | 16.359 | 20.2656 | 22.9671 | 26.0878 | 16.9192
2627 | 24.1768 | 21.8735 | 18.2207 | 12.9452 | 8.9677 | 7.2312 | 8.0034 | 11.2875 | 15.7307 | 20.0978 | 22.5209 | 25.8805 | 16.4113
2628 | 24.6666 | 22.3811 | 18.7656 | 13.1791 | 9.2327 | 7.5298 | 8.7364 | 12.4999 | 16.3578 | 20.245 | 23.0742 | 26.4105 | 16.9232
2629 | 24.9937 | 22.6852 | 18.9619 | 13.3654 | 9.3653 | 7.6111 | 8.7627 | 12.445 | 16.1766 | 20.2233 | 23.1404 | 26.7871 | 17.0432
2630 | 23.8936 | 21.3573 | 18.2069 | 13.3053 | 9.1881 | 7.5888 | 8.7517 | 12.4504 | 16.1339 | 19.8151 | 22.56 | 25.5717 | 16.5686
2631 | 22.7871 | 20.656 | 17.1282 | 12.8564 | 8.8429 | 7.2917 | 8.4378 | 12.2438 | 15.7134 | 19.1623 | 21.8365 | 24.5501 | 15.9588
2632 | 23.6487 | 21.4477 | 17.6783 | 12.5524 | 8.6052 | 7.227 | 8.3285 | 11.9886 | 15.5561 | 19.1563 | 22.5088 | 25.6269 | 16.1937
2633 | 23.983 | 21.5008 | 17.7465 | 12.6613 | 8.7231 | 7.2571 | 8.4925 | 12.0686 | 15.4418 | 19.3768 | 22.1748 | 25.2356 | 16.2218
2640 | 27.2894 | 24.1668 | 20.7209 | 14.0377 | 9.4026 | 6.9084 | 7.9093 | 11.4621 | 15.3896 | 20.6631 | 24.7299 | 28.1966 | 17.573
2641 | 27.2931 | 24.0613 | 20.8308 | 14.0871 | 9.3683 | 6.8878 | 7.8877 | 11.4873 | 15.2296 | 20.6715 | 24.7083 | 28.3027 | 17.568
2642 | 27.7701 | 24.2566 | 21.0916 | 14.8591 | 10.1652 | 7.6748 | 8.5101 | 12.0012 | 15.7642 | 21.3579 | 25.0004 | 28.6418 | 18.0911
2643 | 27.5872 | 24.2771 | 20.9192 | 14.4086 | 9.7334 | 7.2293 | 8.1912 | 11.6105 | 15.3456 | 20.7444 | 25.1198 | 28.5589 | 17.8104
2644 | 27.1549 | 23.9698 | 20.5725 | 14.2229 | 9.4302 | 7.0005 | 7.9667 | 11.4308 | 15.1652 | 20.2974 | 24.7947 | 28.2552 | 17.5217
2645 | 27.8879 | 24.3065 | 21.2248 | 14.9211 | 10.3414 | 7.8819 | 8.7766 | 12.3175 | 16.09 | 21.8479 | 25.2861 | 28.8173 | 18.3083
2646 | 27.6545 | 24.3722 | 21.1493 | 14.7406 | 10.0412 | 7.6237 | 8.5124 | 11.8841 | 15.6557 | 21.1639 | 25.212 | 28.6363 | 18.0538
2647 | 27.4894 | 23.9978 | 21.1873 | 14.4933 | 9.699 | 7.3469 | 8.2609 | 11.7644 | 15.6187 | 20.9992 | 25.053 | 28.2831 | 17.8494
2648 | 28.6816 | 24.8902 | 22.1596 | 15.8621 | 11.0781 | 9.1887 | 9.9164 | 13.9564 | 17.8161 | 22.6509 | 25.8296 | 28.7184 | 19.229
2649 | 25.0225 | 22.1735 | 18.9262 | 13.0903 | 8.3503 | 6.2568 | 6.9995 | 9.4666 | 13.1714 | 18.0368 | 22.3018 | 26.4661 | 15.8551
2650 | 27.7243 | 24.2369 | 21.1125 | 14.7752 | 10.0602 | 7.4301 | 8.5326 | 12.107 | 15.8017 | 21.2923 | 24.8164 | 28.5646 | 18.0378
2651 | 27.9307 | 24.4286 | 21.2143 | 14.8974 | 10.1042 | 7.5038 | 8.5998 | 12.0447 | 15.7397 | 21.3607 | 24.9691 | 28.5326 | 18.1105
2652 | 28.2874 | 24.3439 | 21.9267 | 15.8183 | 11.0494 | 9.0627 | 10.0002 | 13.5951 | 17.6618 | 22.385 | 25.5589 | 28.7916 | 19.0401
2653 | 26.362 | 23.0729 | 20.0168 | 13.8114 | 9.0321 | 6.7327 | 7.7091 | 10.801 | 14.287 | 19.4006 | 23.2777 | 27.595 | 16.8415
2655 | 27.9446 | 24.3373 | 21.1537 | 14.8495 | 10.1566 | 7.5998 | 8.562 | 11.997 | 15.7919 | 21.3678 | 24.9489 | 28.677 | 18.1155
2656 | 28.0442 | 24.4745 | 21.3163 | 15.0516 | 10.2684 | 7.8469 | 8.6906 | 12.2003 | 15.9605 | 21.7515 | 25.1634 | 28.6861 | 18.2879
2658 | 27.8475 | 24.42 | 21.2107 | 14.8802 | 10.0346 | 7.5459 | 8.4154 | 12.0068 | 15.786 | 21.238 | 25.1784 | 28.6823 | 18.1038
2659 | 27.5462 | 24.2466 | 20.9906 | 14.5713 | 9.8734 | 7.2995 | 8.1935 | 11.7032 | 15.4405 | 20.9749 | 25.2085 | 28.6054 | 17.8878
2660 | 27.6308 | 24.2786 | 20.8517 | 14.5643 | 9.847 | 7.3042 | 8.2467 | 11.736 | 15.2626 | 20.9803 | 25.0398 | 28.3887 | 17.8442
2661 | 27.9495 | 24.224 | 21.2738 | 14.8499 | 10.0847 | 7.5636 | 8.6078 | 12.1336 | 15.9409 | 21.3391 | 25.094 | 28.5824 | 18.1369
2663 | 27.8737 | 24.3923 | 21.1848 | 15.0345 | 10.3957 | 7.8374 | 8.8512 | 12.1781 | 15.9632 | 21.0673 | 24.863 | 28.4342 | 18.173
2665 | 28.133 | 24.3241 | 21.5368 | 15.5709 | 10.8317 | 8.5909 | 9.4486 | 12.9774 | 16.8672 | 21.9311 | 25.2061 | 28.66 | 18.6731
2666 | 27.8736 | 24.1244 | 21.4431 | 15.4201 | 10.6356 | 8.2571 | 9.1468 | 12.6584 | 16.6826 | 21.4111 | 24.9682 | 28.3968 | 18.4182
2668 | 27.9046 | 24.1944 | 21.537 | 15.6099 | 10.9604 | 8.5597 | 9.466 | 12.8617 | 16.8792 | 21.84 | 24.8814 | 28.337 | 18.5859
2669 | 28.0912 | 24.266 | 21.7733 | 15.7908 | 11.2164 | 8.9479 | 9.8238 | 13.2419 | 17.3723 | 22.2409 | 25.2669 | 28.5772 | 18.884
2671 | 27.8762 | 24.2115 | 21.7017 | 15.6961 | 10.993 | 8.8095 | 9.7258 | 13.2136 | 17.3612 | 22.1026 | 25.0804 | 28.3495 | 18.7601
2672 | 28.2303 | 24.5711 | 22.0451 | 15.9955 | 11.4103 | 9.2008 | 9.9832 | 13.502 | 17.8314 | 22.4709 | 25.5652 | 28.5042 | 19.1092
2675 | 28.0394 | 24.1623 | 21.8907 | 16.2047 | 11.3668 | 9.4191 | 10.3424 | 13.8042 | 17.9438 | 22.3397 | 25.3545 | 28.2595 | 19.0939
2678 | 27.8467 | 24.4485 | 21.2653 | 14.928 | 10.2367 | 7.6629 | 8.6949 | 12.1026 | 15.7968 | 21.4247 | 25.1144 | 28.5848 | 18.1755
2680 | 28.3873 | 24.6402 | 21.7405 | 15.5319 | 10.9288 | 8.6048 | 9.4848 | 13.1012 | 17.1688 | 22.2617 | 25.7249 | 28.6386 | 18.8511
2681 | 28.0226 | 24.2926 | 21.6407 | 15.4799 | 10.7513 | 8.565 | 9.323 | 13.1103 | 17.1435 | 22.051 | 25.4927 | 28.4574 | 18.6942
2700 | 27.8956 | 24.1791 | 21.3549 | 15.2302 | 10.4512 | 8.0893 | 9.0654 | 12.7943 | 16.5625 | 21.7985 | 25.3792 | 28.7863 | 18.4655
2701 | 27.8548 | 24.3234 | 21.3742 | 15.176 | 10.5158 | 7.9673 | 8.8995 | 12.2997 | 16.1154 | 21.3383 | 24.9884 | 28.4675 | 18.2767
2702 | 28 | 24.2985 | 21.451 | 15.2285 | 10.5228 | 7.979 | 8.8917 | 12.3818 | 16.2349 | 21.538 | 25.2334 | 28.6654 | 18.3687
2703 | 28.1466 | 24.2935 | 21.5965 | 15.2837 | 10.6151 | 8.2761 | 9.2171 | 12.8345 | 16.7922 | 22.0054 | 25.6538 | 28.9973 | 18.6426
2705 | 27.981 | 24.4131 | 21.6437 | 15.2513 | 10.7506 | 8.4672 | 9.3063 | 12.9964 | 16.8172 | 22.214 | 25.6653 | 28.5815 | 18.674
2706 | 27.9964 | 24.2996 | 21.5835 | 15.3084 | 10.6041 | 8.385 | 9.2365 | 12.9415 | 17.0092 | 22.1445 | 25.5524 | 28.8508 | 18.6593
2707 | 28.127 | 24.5424 | 21.4614 | 15.1541 | 10.7812 | 8.5545 | 9.4453 | 13.1642 | 16.9739 | 22.1628 | 25.4967 | 28.8565 | 18.7267
2710 | 27.9826 | 23.9953 | 21.296 | 15.0361 | 10.225 | 8.1288 | 8.9048 | 12.6266 | 16.5071 | 21.905 | 25.4895 | 28.6145 | 18.3926
2711 | 28.0121 | 24.2948 | 21.7015 | 15.697 | 10.9777 | 9.0159 | 9.8582 | 13.4914 | 17.4738 | 22.4513 | 25.6253 | 28.8757 | 18.9562
2712 | 27.6968 | 24.2279 | 21.2759 | 14.7774 | 10.152 | 7.7062 | 8.5603 | 12.0526 | 15.9904 | 21.4087 | 25.3375 | 28.7082 | 18.1578
2713 | 28.0445 | 24.3096 | 21.4639 | 14.873 | 10.1879 | 7.8925 | 8.7595 | 12.365 | 16.1963 | 21.7775 | 25.5042 | 28.7314 | 18.3421
2714 | 27.824 | 24.1253 | 21.2743 | 14.6864 | 10.0071 | 7.6682 | 8.6017 | 12.2118 | 16.1301 | 21.5272 | 25.3373 | 28.6245 | 18.1682
2715 | 28.2325 | 24.4882 | 21.782 | 15.8409 | 10.992 | 9.0904 | 9.834 | 13.6588 | 17.4382 | 22.536 | 25.8499 | 28.8225 | 19.0471
2716 | 27.8545 | 24.248 | 21.2972 | 15.016 | 10.4989 | 8.2219 | 9.1076 | 12.728 | 16.5825 | 21.8395 | 25.4512 | 28.9462 | 18.4826
2717 | 28.4596 | 24.5743 | 21.7811 | 15.8035 | 10.8158 | 8.7871 | 9.5348 | 13.413 | 17.2007 | 22.2765 | 25.47 | 28.5761 | 18.891
2720 | 25.6406 | 22.6718 | 19.5336 | 13.9177 | 9.075 | 6.8819 | 7.8553 | 10.9914 | 14.4404 | 19.1576 | 22.9915 | 27.2501 | 16.7006
2721 | 27.5621 | 23.8877 | 21.3329 | 15.4976 | 10.6243 | 8.405 | 9.2808 | 12.8354 | 16.8471 | 21.5591 | 24.6165 | 28.0793 | 18.3773
2722 | 27.2922 | 24.0156 | 20.815 | 14.7208 | 9.9347 | 7.3105 | 8.3999 | 11.857 | 15.5306 | 20.638 | 24.3589 | 28.2896 | 17.7636
2725 | 27.6869 | 24.0826 | 21.2499 | 15.1014 | 10.4493 | 8.156 | 9.0571 | 12.3474 | 16.2169 | 21.0919 | 24.827 | 28.2799 | 18.2122
2726 | 27.477 | 24.1968 | 20.7572 | 14.9007 | 10.2548 | 7.8002 | 8.7065 | 12.0838 | 15.9539 | 20.7589 | 24.483 | 27.9633 | 17.9447
2727 | 27.5465 | 24.2903 | 20.8971 | 14.7542 | 10.1222 | 7.5995 | 8.5155 | 12.0144 | 15.6929 | 20.7452 | 24.4749 | 28.251 | 17.9086
2729 | 27.3393 | 23.8778 | 20.7044 | 14.6133 | 9.7675 | 7.2899 | 8.3235 | 11.7392 | 15.2394 | 20.7423 | 24.5261 | 28.3012 | 17.7053
2730 | 26.5865 | 23.2904 | 20.155 | 14.0142 | 9.1519 | 7.0149 | 7.9029 | 11.3017 | 14.7546 | 19.9164 | 23.6683 | 27.7805 | 17.1281
2731 | 27.6046 | 24.1636 | 21.0905 | 14.8915 | 10.1007 | 7.7393 | 8.5404 | 12.2508 | 15.8996 | 21.4811 | 25.2678 | 28.532 | 18.1302
2732 | 27.8592 | 24.2556 | 21.4235 | 15.095 | 10.251 | 8.0908 | 8.7861 | 12.5674 | 16.3231 | 21.6867 | 25.4456 | 28.4328 | 18.3514
2733 | 28.1308 | 24.2042 | 21.4227 | 15.1495 | 10.5215 | 8.5762 | 9.2599 | 13.0489 | 16.7982 | 22.146 | 25.766 | 28.9132 | 18.6614
2735 | 28.0018 | 24.304 | 21.4568 | 15.2281 | 10.3431 | 8.2292 | 8.8313 | 12.6599 | 16.4526 | 21.9478 | 25.4193 | 28.3302 | 18.4337
2736 | 28.0625 | 24.246 | 21.4674 | 15.3768 | 10.4516 | 8.3997 | 9.066 | 12.7887 | 16.7233 | 22.0498 | 25.4968 | 28.392 | 18.5434
2737 | 28.3564 | 24.3763 | 21.6276 | 15.7477 | 10.7622 | 8.7386 | 9.4332 | 13.4372 | 17.1386 | 22.2932 | 25.4474 | 28.749 | 18.8423
2738 | 28.3612 | 24.6738 | 21.9571 | 15.6463 | 10.6717 | 8.7329 | 9.5076 | 13.489 | 17.3031 | 22.314 | 25.4114 | 28.5011 | 18.8808
2739 | 28.491 | 24.7719 | 21.8711 | 15.7419 | 10.8598 | 8.8243 | 9.5758 | 13.4407 | 17.1688 | 22.2322 | 25.6048 | 28.6398 | 18.9352
2745 | 22.3653 | 19.5431 | 16.771 | 13.8866 | 10.2315 | 9.1774 | 10.1931 | 13.6746 | 16.9622 | 19.842 | 20.7154 | 23.0073 | 16.3641
2747 | 22.3503 | 19.4437 | 16.7424 | 14.0264 | 10.2955 | 9.1439 | 10.1016 | 13.6116 | 16.9215 | 19.7998 | 20.6916 | 22.9975 | 16.3438
2748 | 22.4495 | 19.5128 | 16.7915 | 13.93 | 10.2525 | 9.1193 | 10.1346 | 13.6332 | 16.9016 | 19.7814 | 20.7309 | 23.0344 | 16.356
2749 | 22.084 | 19.3494 | 16.7506 | 14.0657 | 10.2569 | 9.1185 | 10.1236 | 13.7144 | 16.9718 | 19.9645 | 20.5042 | 22.775 | 16.3066
2750 | 22.2004 | 19.3407 | 16.7784 | 14.0643 | 10.2596 | 9.1393 | 10.1466 | 13.6946 | 16.9681 | 19.7817 | 20.4366 | 22.7723 | 16.2985
2752 | 21.9591 | 19.1997 | 16.5684 | 13.9473 | 10.1482 | 9.1228 | 10.1255 | 13.5224 | 16.6797 | 19.664 | 20.2887 | 22.7224 | 16.1623
2753 | 22.0217 | 19.318 | 16.5034 | 14.0527 | 10.3334 | 9.168 | 10.2194 | 13.6882 | 16.8825 | 19.8864 | 20.2748 | 22.6477 | 16.2497
2754 | 22.2003 | 19.3857 | 16.5785 | 14.1946 | 10.2701 | 9.1684 | 10.1915 | 13.6716 | 16.8852 | 19.7255 | 20.1235 | 22.7639 | 16.2632
2756 | 22.2564 | 19.2089 | 16.6896 | 14.203 | 10.3457 | 9.2502 | 10.266 | 13.8483 | 17.1047 | 20.0673 | 20.5697 | 23.089 | 16.4082
2757 | 21.9816 | 19.1134 | 16.4458 | 14.0627 | 10.2393 | 9.1711 | 10.2258 | 13.6826 | 16.9219 | 19.7268 | 20.0718 | 22.5333 | 16.1813
2758 | 21.3154 | 18.274 | 15.9874 | 13.7056 | 9.8912 | 9.0336 | 10.0171 | 13.6431 | 17.0501 | 19.7896 | 20.0941 | 22.4079 | 15.9341
2759 | 22.6513 | 19.6552 | 16.8064 | 13.9536 | 10.2663 | 9.0592 | 10.0645 | 13.5738 | 16.9311 | 19.7952 | 20.8394 | 23.208 | 16.4003
2760 | 22.5941 | 19.6301 | 16.7309 | 13.9867 | 10.2687 | 9.1248 | 10.0614 | 13.5682 | 16.9374 | 19.845 | 20.8673 | 23.188 | 16.4002
2761 | 22.7724 | 19.785 | 16.8036 | 14.0135 | 10.2122 | 9.122 | 10.0668 | 13.5688 | 16.942 | 19.9519 | 20.9837 | 23.3384 | 16.4634
2762 | 22.7854 | 19.7325 | 16.7935 | 14.0438 | 10.2457 | 9.1155 | 10.0587 | 13.6593 | 16.9529 | 19.9886 | 20.8955 | 23.3258 | 16.4664
2763 | 22.9297 | 19.8445 | 16.8578 | 14.0131 | 10.2135 | 9.1206 | 10.0719 | 13.5327 | 16.8936 | 19.9001 | 20.8967 | 23.3661 | 16.47
2765 | 22.682 | 19.786 | 16.7478 | 14.0363 | 10.2253 | 9.1038 | 10.0673 | 13.6832 | 16.9089 | 19.9591 | 20.7345 | 23.03 | 16.4137
2766 | 22.7536 | 19.8535 | 16.7417 | 13.9688 | 10.1877 | 9.0841 | 10.0513 | 13.5775 | 16.948 | 19.9041 | 20.9556 | 23.4312 | 16.4548
2767 | 22.7724 | 19.785 | 16.8036 | 14.0135 | 10.2122 | 9.122 | 10.0668 | 13.5688 | 16.942 | 19.9519 | 20.9837 | 23.3384 | 16.4634
2768 | 22.9559 | 19.7909 | 16.8447 | 14.0381 | 10.1514 | 9.1351 | 10.0694 | 13.4742 | 16.8659 | 19.8268 | 20.8858 | 23.2717 | 16.4425
2769 | 22.8465 | 19.789 | 16.8524 | 14.0461 | 10.2341 | 9.1101 | 10.0639 | 13.6014 | 16.9421 | 19.8901 | 20.8505 | 23.1844 | 16.4509
2770 | 22.5941 | 19.6301 | 16.7309 | 13.9867 | 10.2687 | 9.1248 | 10.0614 | 13.5682 | 16.9374 | 19.845 | 20.8673 | 23.188 | 16.4002
2773 | 21.9376 | 19.123 | 16.6931 | 14.0679 | 10.2081 | 9.0926 | 10.1416 | 13.6572 | 16.8543 | 19.7476 | 20.2938 | 22.6119 | 16.2024
2774 | 21.6007 | 18.9136 | 16.525 | 14.0214 | 10.1154 | 9.0506 | 10.0944 | 13.6418 | 16.8337 | 19.6921 | 20.2617 | 22.3941 | 16.0954
2775 | 22.2121 | 19.5271 | 16.6379 | 14.1689 | 10.3878 | 9.2741 | 10.2977 | 13.8322 | 17.0455 | 20.0076 | 20.7463 | 22.8591 | 16.4164
2776 | 21.5685 | 18.6814 | 16.2627 | 13.9083 | 10.0338 | 9.0656 | 10.0892 | 13.6781 | 16.86 | 19.7427 | 20.1945 | 22.3768 | 16.0385
2777 | 21.6062 | 18.8177 | 16.3943 | 14.0073 | 10.117 | 9.0505 | 10.1018 | 13.6455 | 16.8838 | 19.7263 | 20.2557 | 22.4845 | 16.0909
2778 | 21.3512 | 18.5031 | 16.0942 | 13.7485 | 9.9442 | 8.964 | 10.0738 | 13.689 | 16.8674 | 19.6882 | 20.0288 | 22.1774 | 15.9275
2779 | 21.2984 | 18.3591 | 15.9413 | 13.6438 | 9.9214 | 8.9353 | 9.9794 | 13.6225 | 16.9721 | 19.7134 | 19.9614 | 22.2402 | 15.8824
2780 | 21.9651 | 18.7486 | 16.1646 | 13.8591 | 9.7799 | 8.6744 | 9.6661 | 13.2506 | 16.858 | 19.8563 | 20.6232 | 23.1731 | 16.0516
2782 | 21.3085 | 18.2918 | 15.9559 | 13.6211 | 9.8175 | 8.8919 | 9.9236 | 13.5503 | 16.9629 | 19.8607 | 20.2729 | 22.463 | 15.91
2783 | 21.304 | 18.3126 | 15.9413 | 13.6701 | 9.9221 | 8.9741 | 9.9995 | 13.6128 | 17.0524 | 19.8175 | 20.1284 | 22.3403 | 15.9229
2784 | 21.3251 | 18.3911 | 15.9106 | 13.5907 | 9.8581 | 8.8708 | 9.903 | 13.5176 | 16.9471 | 19.7398 | 20.0552 | 22.4615 | 15.8809
2785 | 22.5506 | 19.2498 | 16.5521 | 13.9327 | 9.8091 | 8.5574 | 9.5666 | 13.0623 | 16.8849 | 19.8634 | 20.8867 | 23.9001 | 16.2346
2786 | 22.3523 | 18.9503 | 16.537 | 13.9129 | 9.8062 | 8.647 | 9.7022 | 13.2408 | 17.0911 | 20.0541 | 20.8462 | 23.7213 | 16.2385
2787 | 22.2046 | 18.8968 | 16.4855 | 13.9169 | 9.8125 | 8.6736 | 9.6112 | 13.3149 | 17.0255 | 20.0734 | 21.0098 | 23.7916 | 16.2347
2790 | 23.5718 | 19.8967 | 17.3999 | 14.2001 | 9.9994 | 8.6078 | 9.4529 | 13.0565 | 16.8613 | 20.4249 | 21.6494 | 25.125 | 16.6871
2791 | 26.7097 | 23.5735 | 20.442 | 14.9732 | 10.4482 | 8.3669 | 9.1525 | 12.4098 | 16.3587 | 20.5696 | 23.9094 | 27.8307 | 17.8954
2792 | 26.758 | 23.6469 | 20.3351 | 14.864 | 10.296 | 8.2083 | 8.9635 | 12.4069 | 16.3924 | 20.6487 | 23.9777 | 28.0266 | 17.877
2793 | 27.0142 | 23.9359 | 20.6654 | 15.0703 | 10.4026 | 8.2908 | 9.0404 | 12.375 | 16.4156 | 20.9061 | 24.1625 | 27.8264 | 18.0088
2794 | 27.5725 | 24.0034 | 20.9752 | 15.3752 | 10.7443 | 8.5805 | 9.4403 | 12.7655 | 16.6157 | 21.199 | 24.7278 | 28.311 | 18.3592
2795 | 26.3926 | 22.7476 | 19.7816 | 14.9046 | 10.5517 | 8.4318 | 9.4936 | 12.9572 | 16.7842 | 20.8591 | 23.5399 | 27.4474 | 17.8243
2797 | 26.7444 | 23.6515 | 20.445 | 14.9852 | 10.3343 | 8.2432 | 9.0188 | 12.4784 | 16.3731 | 20.6735 | 23.9229 | 27.9921 | 17.9052
2798 | 26.8965 | 23.4556 | 20.3047 | 14.9081 | 10.5515 | 8.6377 | 9.3726 | 12.6807 | 16.756 | 20.7241 | 23.7668 | 27.9477 | 18.0002
2799 | 26.9014 | 23.3279 | 20.1909 | 14.8856 | 10.4041 | 8.3549 | 9.2019 | 12.6422 | 16.6912 | 20.6136 | 24.0189 | 27.9281 | 17.9301
2800 | 26.7474 | 23.3072 | 20.3935 | 15.232 | 10.6858 | 8.7274 | 9.5226 | 12.9107 | 17.0664 | 21.1376 | 23.3914 | 27.72 | 18.0702
2803 | 27.2961 | 23.8822 | 20.8924 | 15.1209 | 10.4962 | 8.225 | 9.0801 | 12.5478 | 16.5162 | 21.0696 | 24.1413 | 28.0864 | 18.1129
2804 | 27.1967 | 23.8532 | 20.8842 | 15.2958 | 10.9452 | 8.7175 | 9.6043 | 12.7645 | 16.6962 | 21.3534 | 24.5435 | 28.0948 | 18.3291
2805 | 27.6006 | 24.0183 | 21.0049 | 15.3507 | 10.8164 | 8.5448 | 9.451 | 12.8301 | 16.8995 | 21.6359 | 24.8581 | 28.2246 | 18.4362
2806 | 27.2995 | 23.7374 | 21.0085 | 15.3484 | 10.8673 | 8.807 | 9.6521 | 12.8523 | 17.1234 | 21.5795 | 24.1211 | 28.0527 | 18.3708
2807 | 27.3191 | 24.0392 | 20.8653 | 15.1534 | 10.5471 | 8.3395 | 9.2515 | 12.8203 | 16.6543 | 21.2175 | 24.3432 | 28.0794 | 18.2191
2808 | 26.6947 | 23.6124 | 20.4948 | 14.9622 | 10.1907 | 7.963 | 8.8306 | 12.3925 | 16.503 | 20.8169 | 23.6778 | 27.7592 | 17.8248
2809 | 27.2507 | 23.5538 | 20.7547 | 15.2379 | 10.5849 | 8.3015 | 9.2225 | 12.4926 | 16.4303 | 20.8777 | 24.0001 | 27.7968 | 18.0419
2810 | 27.6217 | 23.7778 | 21.2038 | 15.3662 | 10.5815 | 8.4321 | 9.3228 | 12.7448 | 16.8758 | 21.3813 | 24.5765 | 28.2294 | 18.3428
2820 | 27.2891 | 23.9045 | 21.0287 | 15.7575 | 11.4003 | 9.4221 | 10.2412 | 13.6201 | 17.9444 | 22.0618 | 24.7804 | 28.3286 | 18.8149
2821 | 27.877 | 24.3662 | 21.5447 | 16.2815 | 11.9622 | 9.9904 | 10.8085 | 14.0093 | 18.3913 | 22.6692 | 24.7222 | 28.6762 | 19.2749
2823 | 27.8249 | 24.3186 | 21.7617 | 16.368 | 12.0548 | 10.1486 | 10.9994 | 14.2382 | 18.7021 | 22.7574 | 24.6667 | 28.4928 | 19.3611
2824 | 27.2554 | 24.1149 | 21.8667 | 16.8339 | 12.5679 | 10.4927 | 11.6227 | 15.0152 | 19.2911 | 22.9458 | 24.8686 | 28.5447 | 19.6183
2825 | 27.8267 | 24.0225 | 22.0532 | 16.7207 | 12.1503 | 10.1959 | 11.1764 | 14.6758 | 19.0214 | 22.7715 | 24.8181 | 28.554 | 19.4989
2827 | 26.7071 | 23.6682 | 21.3947 | 16.1926 | 11.9217 | 9.9564 | 10.9826 | 14.3279 | 18.5448 | 22.3513 | 24.5571 | 28.0074 | 19.051
2828 | 26.9954 | 23.9548 | 21.5281 | 16.4727 | 12.4617 | 10.4744 | 11.5076 | 14.8601 | 19.0485 | 22.7507 | 24.9323 | 28.4358 | 19.4518
2829 | 27.202 | 24.1231 | 21.7429 | 16.8386 | 12.7934 | 10.8219 | 11.8396 | 15.184 | 19.5012 | 22.8682 | 25.0914 | 28.4691 | 19.7063
2830 | 27.7146 | 24.1409 | 21.347 | 15.9601 | 11.6393 | 9.5887 | 10.5019 | 13.7648 | 18.2137 | 22.27 | 24.7374 | 28.4443 | 19.0269
2831 | 27.7678 | 24.1434 | 22.2889 | 17.0611 | 12.6273 | 10.6788 | 11.852 | 15.394 | 19.328 | 23.0231 | 25.3798 | 28.6132 | 19.8465
2832 | 27.2342 | 24.1265 | 22.2077 | 17.5083 | 13.3732 | 11.2331 | 12.3972 | 15.8895 | 20.0552 | 23.0441 | 25.0403 | 28.1765 | 20.0238
2833 | 27.0459 | 23.711 | 22.1051 | 17.6214 | 13.476 | 11.4751 | 12.6842 | 16.1609 | 20.1837 | 23.1371 | 25.0192 | 28.1327 | 20.0627
2834 | 27.235 | 24.0206 | 22.3174 | 17.6366 | 13.6679 | 11.6602 | 12.924 | 16.4175 | 20.3328 | 23.2426 | 25.1082 | 28.2125 | 20.2313
2835 | 28.1963 | 24.4457 | 22.7015 | 16.8938 | 12.3375 | 10.3524 | 11.3867 | 15.0874 | 19.0058 | 22.9701 | 25.6328 | 28.8634 | 19.8228
2836 | 28.8408 | 25.1371 | 23.0626 | 17.2633 | 12.7023 | 10.9049 | 11.7806 | 15.6736 | 19.2895 | 23.5013 | 26.0239 | 28.6405 | 20.235
2839 | 27.4804 | 24.1577 | 22.2944 | 17.5277 | 13.466 | 11.3829 | 12.5318 | 16.0324 | 20.0723 | 23.3421 | 25.6067 | 28.2849 | 20.1816
2840 | 27.9695 | 24.5081 | 22.8795 | 17.555 | 13.3126 | 11.389 | 12.4186 | 16.1755 | 20.0259 | 23.1129 | 25.6155 | 28.4787 | 20.2867
2842 | 26.7981 | 23.6007 | 20.8692 | 16.0489 | 11.7494 | 9.9033 | 10.8057 | 14.1957 | 18.2656 | 22.2497 | 24.5282 | 27.8963 | 18.9092
2843 | 26.331 | 23.0402 | 20.2244 | 15.9244 | 11.535 | 9.765 | 10.6713 | 14.0498 | 17.9312 | 21.6394 | 23.9907 | 27.392 | 18.5412
2844 | 26.8682 | 23.627 | 20.8 | 15.9893 | 11.6862 | 9.7814 | 10.6825 | 14.0332 | 18.0113 | 22.0017 | 24.4224 | 28.0423 | 18.8288
2845 | 24.1885 | 20.3524 | 17.7982 | 14.2835 | 10.0618 | 8.6761 | 9.6029 | 13.0895 | 17.0118 | 20.494 | 21.8239 | 25.5584 | 16.9118
2846 | 24.5139 | 20.8086 | 18.0874 | 14.6386 | 10.3403 | 8.6929 | 9.7699 | 13.1811 | 17.1273 | 20.8281 | 22.4 | 25.9039 | 17.191
2847 | 23.9596 | 20.3339 | 17.7914 | 14.4109 | 10.1362 | 8.7236 | 9.6029 | 13.1508 | 16.9446 | 20.5519 | 21.8889 | 25.5934 | 16.924
2848 | 25.3102 | 21.6336 | 18.8029 | 14.8286 | 10.7133 | 9.1219 | 10.0765 | 13.6182 | 17.3627 | 21.172 | 23.3587 | 26.7338 | 17.7277
2849 | 24.6381 | 20.792 | 18.035 | 14.7291 | 10.5456 | 9.059 | 9.9872 | 13.5141 | 17.384 | 20.8067 | 22.2601 | 25.5113 | 17.2719
2850 | 26.6823 | 22.8971 | 19.9052 | 15.2457 | 11.1963 | 9.3278 | 10.2177 | 13.7818 | 17.7595 | 21.6827 | 24.0665 | 27.5651 | 18.3606
2852 | 26.8901 | 23.1798 | 20.5548 | 15.8002 | 11.5035 | 9.5247 | 10.542 | 13.9043 | 17.9198 | 21.9704 | 24.3562 | 27.7649 | 18.6592
2864 | 27.0337 | 23.6398 | 20.856 | 15.328 | 10.7399 | 8.7206 | 9.5312 | 12.7405 | 17.0028 | 21.2665 | 23.906 | 28.0126 | 18.2315
2865 | 27.1919 | 23.5542 | 20.9173 | 15.491 | 11.0068 | 8.8714 | 9.7978 | 13.0544 | 17.1783 | 21.4162 | 24.352 | 28.2981 | 18.4275
2866 | 27.1963 | 23.8265 | 20.8499 | 15.3921 | 11.0051 | 9.0398 | 9.9067 | 13.1917 | 17.541 | 21.8326 | 24.4974 | 28.3236 | 18.5502
2867 | 27.3372 | 23.96 | 20.9477 | 15.6344 | 11.2569 | 9.1741 | 10.0946 | 13.4011 | 17.546 | 21.871 | 24.6712 | 28.5772 | 18.706
2868 | 27.5245 | 24.1192 | 20.9387 | 15.7503 | 11.3147 | 9.3822 | 10.2886 | 13.4567 | 17.6635 | 21.8727 | 24.4065 | 28.4583 | 18.7647
2869 | 27.874 | 24.2567 | 21.4878 | 16.1458 | 11.4458 | 9.5041 | 10.3929 | 13.8575 | 18.212 | 22.4017 | 24.792 | 28.5532 | 19.077
2870 | 27.6769 | 24.195 | 21.2092 | 15.7279 | 11.1624 | 9.0937 | 9.8967 | 13.1869 | 17.6136 | 22.1087 | 24.5886 | 28.4191 | 18.7399
2871 | 28.0789 | 24.3936 | 21.5622 | 15.8556 | 11.1039 | 8.8723 | 9.7877 | 13.2202 | 17.4619 | 22.0978 | 25.2951 | 28.3829 | 18.8427
2873 | 27.9649 | 24.2549 | 21.9323 | 16.3499 | 11.9341 | 9.9247 | 10.8722 | 14.3006 | 18.7293 | 22.8006 | 24.8616 | 28.5572 | 19.3735
2874 | 28.0414 | 24.185 | 21.7954 | 16.2428 | 11.6842 | 9.747 | 10.6427 | 13.9297 | 18.369 | 22.7299 | 24.9279 | 28.5029 | 19.2332
2875 | 27.9629 | 24.1771 | 21.8438 | 16.1702 | 11.5432 | 9.5162 | 10.4099 | 13.8496 | 18.1458 | 22.6384 | 25.0413 | 28.4174 | 19.143
2876 | 27.7477 | 23.9729 | 21.6716 | 15.9626 | 11.2772 | 9.0748 | 10.0662 | 13.4448 | 17.9267 | 22.2867 | 24.9922 | 28.4023 | 18.9021
2877 | 27.9688 | 24.2365 | 22.0547 | 16.1007 | 11.7328 | 9.5799 | 10.5495 | 13.9883 | 18.3019 | 22.6894 | 25.1548 | 28.3707 | 19.2273
2878 | 28.4607 | 24.4708 | 22.2966 | 16.4281 | 11.5321 | 9.7282 | 10.6248 | 14.4477 | 18.2814 | 22.8429 | 25.6914 | 28.5871 | 19.4493
2879 | 28.6335 | 24.7418 | 22.7063 | 16.7576 | 11.847 | 10.0372 | 10.9534 | 14.9505 | 18.6804 | 23.1743 | 26.1355 | 28.7744 | 19.7827
2880 | 28.4546 | 25.2164 | 23.3705 | 17.2585 | 12.7632 | 10.8993 | 11.711 | 15.514 | 19.5693 | 23.8751 | 26.3401 | 28.7416 | 20.3095
2898
2900 | 25.1015 | 22.5153 | 19.0546 | 14.0472 | 9.9528 | 8.0146 | 9.1715 | 12.7546 | 16.553 | 20.5242 | 23.611 | 26.8987 | 17.3499
2902 | 25.2612 | 22.7136 | 19.1411 | 14.0901 | 10.0147 | 7.9699 | 9.0367 | 12.7098 | 16.4524 | 20.6223 | 23.65 | 27.196 | 17.4048
2903 | 25.3206 | 22.669 | 19.134 | 14.1363 | 10.0512 | 8.0505 | 9.0779 | 12.7409 | 16.4325 | 20.6324 | 23.7083 | 27.1965 | 17.4292
2904 | 25.3206 | 22.669 | 19.134 | 14.1363 | 10.0512 | 8.0505 | 9.0779 | 12.7409 | 16.4325 | 20.6324 | 23.7083 | 27.1965 | 17.4292
2905 | 25.2653 | 22.5963 | 19.0594 | 14.0665 | 10.0105 | 8.0613 | 9.1054 | 12.7701 | 16.4875 | 20.606 | 23.7618 | 27.0812 | 17.4059
2906 | 25.2653 | 22.5963 | 19.0594 | 14.0665 | 10.0105 | 8.0613 | 9.1054 | 12.7701 | 16.4875 | 20.606 | 23.7618 | 27.0812 | 17.4059
2911 | 25.8049 | 23.0577 | 19.4344 | 14.2404 | 10.089 | 8.0577 | 9.0008 | 12.7058 | 16.6161 | 20.766 | 23.9119 | 27.4797 | 17.597
2912 | 25.8049 | 23.0577 | 19.4344 | 14.2404 | 10.089 | 8.0577 | 9.0008 | 12.7058 | 16.6161 | 20.766 | 23.9119 | 27.4797 | 17.597
2913 | 25.9279 | 23.1012 | 19.5566 | 14.223 | 10.1106 | 7.9824 | 8.9852 | 12.6831 | 16.6011 | 20.8 | 24.0871 | 27.4832 | 17.6285
2914 | 25.9594 | 23.1677 | 19.5171 | 14.2308 | 9.9936 | 7.9935 | 8.9711 | 12.6461 | 16.5299 | 20.7707 | 23.9231 | 27.6224 | 17.6105
3000 | 23.9201 | 21.1164 | 16.9196 | 11.4199 | 7.4167 | 6.0701 | 6.9316 | 10.1342 | 13.3128 | 17.3896 | 21.4411 | 24.1748 | 15.0206
3002 | 23.938 | 21.0178 | 16.8426 | 11.3998 | 7.417 | 6.0412 | 6.8579 | 10.0728 | 13.1859 | 17.4029 | 21.4876 | 24.28 | 14.9953
3003 | 23.8641 | 21.0519 | 16.959 | 11.4222 | 7.4261 | 6.1132 | 7.0261 | 10.1761 | 13.3698 | 17.4753 | 21.4757 | 24.0048 | 15.0304
3004 | 24.0628 | 21.1252 | 16.8637 | 11.3486 | 7.3687 | 6.0131 | 6.8627 | 10.1067 | 13.1488 | 17.5799 | 21.6054 | 24.3963 | 15.0402
3005 | 23.9201 | 21.1164 | 16.9196 | 11.4199 | 7.4167 | 6.0701 | 6.9316 | 10.1342 | 13.3128 | 17.3896 | 21.4411 | 24.1748 | 15.0206
3006 | 24.0437 | 21.1551 | 16.9355 | 11.3803 | 7.2917 | 6.0476 | 6.9356 | 10.2355 | 13.2996 | 17.784 | 21.706 | 24.3783 | 15.0994
3008 | 23.9201 | 21.1164 | 16.9196 | 11.4199 | 7.4167 | 6.0701 | 6.9316 | 10.1342 | 13.3128 | 17.3896 | 21.4411 | 24.1748 | 15.0206
3010 | 23.9201 | 21.1164 | 16.9196 | 11.4199 | 7.4167 | 6.0701 | 6.9316 | 10.1342 | 13.3128 | 17.3896 | 21.4411 | 24.1748 | 15.0206
3011 | 23.8641 | 21.0519 | 16.959 | 11.4222 | 7.4261 | 6.1132 | 7.0261 | 10.1761 | 13.3698 | 17.4753 | 21.4757 | 24.0048 | 15.0304
3012 | 23.7922 | 20.9967 | 16.9642 | 11.4427 | 7.4959 | 6.1402 | 7.0317 | 10.2548 | 13.5054 | 17.5153 | 21.4091 | 23.8885 | 15.0364
3013 | 23.8641 | 21.0519 | 16.959 | 11.4222 | 7.4261 | 6.1132 | 7.0261 | 10.1761 | 13.3698 | 17.4753 | 21.4757 | 24.0048 | 15.0304
3015 | 23.985 | 21.0146 | 17.1013 | 11.4161 | 7.345 | 6.1022 | 7.0274 | 10.2412 | 13.406 | 17.7317 | 21.6997 | 24.1034 | 15.0978
3016 | 23.985 | 21.0146 | 17.1013 | 11.4161 | 7.345 | 6.1022 | 7.0274 | 10.2412 | 13.406 | 17.7317 | 21.6997 | 24.1034 | 15.0978
3018 | 23.8138 | 20.9648 | 17.115 | 11.44 | 7.4936 | 6.1901 | 7.1151 | 10.2633 | 13.7314 | 17.7312 | 21.4702 | 23.9515 | 15.1067
3019 | 23.7922 | 20.9967 | 16.9642 | 11.4427 | 7.4959 | 6.1402 | 7.0317 | 10.2548 | 13.5054 | 17.5153 | 21.4091 | 23.8885 | 15.0364
3020 | 23.6782 | 20.914 | 16.9426 | 11.3933 | 7.5381 | 6.1772 | 7.0787 | 10.2564 | 13.5757 | 17.4966 | 21.3377 | 23.9077 | 15.0247
3021 | 23.6388 | 20.8347 | 16.974 | 11.4986 | 7.485 | 6.1401 | 7.0084 | 10.2745 | 13.5756 | 17.4764 | 21.294 | 23.8156 | 15.0013
3022 | 23.6388 | 20.8347 | 16.974 | 11.4986 | 7.485 | 6.1401 | 7.0084 | 10.2745 | 13.5756 | 17.4764 | 21.294 | 23.8156 | 15.0013
3023 | 23.7223 | 20.8725 | 16.9546 | 11.4299 | 7.5146 | 6.2151 | 7.0747 | 10.3543 | 13.673 | 17.5533 | 21.2533 | 23.8092 | 15.0356
3024 | 23.5889 | 20.9009 | 16.8185 | 11.5297 | 7.7644 | 6.2694 | 7.2168 | 10.4062 | 13.7986 | 17.7651 | 21.5858 | 23.9589 | 15.1336
3025 | 23.9409 | 21.0203 | 17.1477 | 11.4328 | 7.4175 | 6.1461 | 7.0675 | 10.2154 | 13.611 | 17.7761 | 21.5782 | 24.0634 | 15.1181
3026 | 23.8138 | 20.9648 | 17.115 | 11.44 | 7.4936 | 6.1901 | 7.1151 | 10.2633 | 13.7314 | 17.7312 | 21.4702 | 23.9515 | 15.1067
3027 | 23.7109 | 21.0449 | 17.1048 | 11.3985 | 7.5813 | 6.2242 | 7.1479 | 10.3136 | 13.8286 | 17.7493 | 21.5149 | 23.9313 | 15.1292
3028 | 23.7109 | 21.0449 | 17.1048 | 11.3985 | 7.5813 | 6.2242 | 7.1479 | 10.3136 | 13.8286 | 17.7493 | 21.5149 | 23.9313 | 15.1292
3029 | 23.7356 | 21.0013 | 17.1241 | 11.4843 | 7.6529 | 6.2738 | 7.1962 | 10.316 | 13.785 | 17.8379 | 21.6419 | 23.9243 | 15.1645
3030 | 23.92 | 21.075 | 17.3186 | 11.5764 | 7.5015 | 6.1796 | 7.1712 | 10.3457 | 14.0469 | 18.1454 | 21.8789 | 24.1004 | 15.2716
3031 | 23.8641 | 21.0519 | 16.959 | 11.4222 | 7.4261 | 6.1132 | 7.0261 | 10.1761 | 13.3698 | 17.4753 | 21.4757 | 24.0048 | 15.0304
3032 | 23.7152 | 21.046 | 16.9578 | 11.4164 | 7.4192 | 6.1256 | 6.9641 | 10.2161 | 13.274 | 17.3412 | 21.3594 | 23.9914 | 14.9855
3033 | 23.6229 | 20.9616 | 16.9339 | 11.4952 | 7.4582 | 6.1444 | 7.0049 | 10.2413 | 13.3932 | 17.4324 | 21.3205 | 23.8088 | 14.9848
3034 | 23.6229 | 20.9616 | 16.9339 | 11.4952 | 7.4582 | 6.1444 | 7.0049 | 10.2413 | 13.3932 | 17.4324 | 21.3205 | 23.8088 | 14.9848
3036 | 23.6352 | 20.8504 | 16.8634 | 11.4793 | 7.535 | 6.1335 | 7.0062 | 10.343 | 13.5998 | 17.5738 | 21.2956 | 23.7838 | 15.0083
3037 | 23.5897 | 20.841 | 16.9074 | 11.4383 | 7.5416 | 6.2216 | 7.0648 | 10.4812 | 13.7028 | 17.6947 | 21.3004 | 23.8411 | 15.052
3038 | 23.6352 | 20.8504 | 16.8634 | 11.4793 | 7.535 | 6.1335 | 7.0062 | 10.343 | 13.5998 | 17.5738 | 21.2956 | 23.7838 | 15.0083
3039 | 23.7152 | 21.046 | 16.9578 | 11.4164 | 7.4192 | 6.1256 | 6.9641 | 10.2161 | 13.274 | 17.3412 | 21.3594 | 23.9914 | 14.9855
3040 | 23.7152 | 21.046 | 16.9578 | 11.4164 | 7.4192 | 6.1256 | 6.9641 | 10.2161 | 13.274 | 17.3412 | 21.3594 | 23.9914 | 14.9855
3041 | 23.7152 | 21.046 | 16.9578 | 11.4164 | 7.4192 | 6.1256 | 6.9641 | 10.2161 | 13.274 | 17.3412 | 21.3594 | 23.9914 | 14.9855
3042 | 23.7152 | 21.046 | 16.9578 | 11.4164 | 7.4192 | 6.1256 | 6.9641 | 10.2161 | 13.274 | 17.3412 | 21.3594 | 23.9914 | 14.9855
3043 | 23.6991 | 21.0475 | 16.9882 | 11.4662 | 7.4432 | 6.0817 | 6.9297 | 10.2444 | 13.408 | 17.4458 | 21.3196 | 23.9746 | 15.004
3044 | 23.8071 | 21.1096 | 16.9249 | 11.4535 | 7.4296 | 6.0779 | 6.9123 | 10.2105 | 13.2754 | 17.3863 | 21.4035 | 24.1322 | 15.0102
3045 | 23.6336 | 20.9702 | 16.9034 | 11.4875 | 7.4774 | 6.0774 | 6.9281 | 10.2862 | 13.503 | 17.5207 | 21.2677 | 23.8272 | 14.9902
3046 | 23.7902 | 21.1445 | 17.0067 | 11.4803 | 7.4839 | 6.0671 | 6.8896 | 10.2537 | 13.2974 | 17.3674 | 21.4117 | 24.1809 | 15.0311
3047 | 23.7902 | 21.1445 | 17.0067 | 11.4803 | 7.4839 | 6.0671 | 6.8896 | 10.2537 | 13.2974 | 17.3674 | 21.4117 | 24.1809 | 15.0311
3048 | 23.8269 | 21.2629 | 17.0658 | 11.5367 | 7.4929 | 6.0705 | 6.922 | 10.1908 | 13.3464 | 17.5332 | 21.3923 | 24.2372 | 15.0731
3049 | 23.7794 | 21.1836 | 17.0814 | 11.5708 | 7.4827 | 6.0408 | 6.9451 | 10.2551 | 13.494 | 17.5842 | 21.4162 | 24.1564 | 15.0825
3051 | 23.9201 | 21.1164 | 16.9196 | 11.4199 | 7.4167 | 6.0701 | 6.9316 | 10.1342 | 13.3128 | 17.3896 | 21.4411 | 24.1748 | 15.0206
3052 | 23.9201 | 21.1164 | 16.9196 | 11.4199 | 7.4167 | 6.0701 | 6.9316 | 10.1342 | 13.3128 | 17.3896 | 21.4411 | 24.1748 | 15.0206
3053 | 23.9201 | 21.1164 | 16.9196 | 11.4199 | 7.4167 | 6.0701 | 6.9316 | 10.1342 | 13.3128 | 17.3896 | 21.4411 | 24.1748 | 15.0206
3054 | 23.9201 | 21.1164 | 16.9196 | 11.4199 | 7.4167 | 6.0701 | 6.9316 | 10.1342 | 13.3128 | 17.3896 | 21.4411 | 24.1748 | 15.0206
3055 | 23.8071 | 21.1096 | 16.9249 | 11.4535 | 7.4296 | 6.0779 | 6.9123 | 10.2105 | 13.2754 | 17.3863 | 21.4035 | 24.1322 | 15.0102
3056 | 23.8071 | 21.1096 | 16.9249 | 11.4535 | 7.4296 | 6.0779 | 6.9123 | 10.2105 | 13.2754 | 17.3863 | 21.4035 | 24.1322 | 15.0102
3057 | 23.8731 | 21.0291 | 16.8323 | 11.3821 | 7.4207 | 6.0012 | 6.8268 | 10.1932 | 13.1883 | 17.439 | 21.4552 | 24.1937 | 14.9862
3058 | 23.8071 | 21.1096 | 16.9249 | 11.4535 | 7.4296 | 6.0779 | 6.9123 | 10.2105 | 13.2754 | 17.3863 | 21.4035 | 24.1322 | 15.0102
3059 | 23.7794 | 21.1836 | 17.0814 | 11.5708 | 7.4827 | 6.0408 | 6.9451 | 10.2551 | 13.494 | 17.5842 | 21.4162 | 24.1564 | 15.0825
3060 | 23.7902 | 21.1445 | 17.0067 | 11.4803 | 7.4839 | 6.0671 | 6.8896 | 10.2537 | 13.2974 | 17.3674 | 21.4117 | 24.1809 | 15.0311
3061 | 23.8269 | 21.2629 | 17.0658 | 11.5367 | 7.4929 | 6.0705 | 6.922 | 10.1908 | 13.3464 | 17.5332 | 21.3923 | 24.2372 | 15.0731
3062 | 23.8269 | 21.2629 | 17.0658 | 11.5367 | 7.4929 | 6.0705 | 6.922 | 10.1908 | 13.3464 | 17.5332 | 21.3923 | 24.2372 | 15.0731
3063 | 23.8926 | 21.1936 | 17.2219 | 11.5861 | 7.581 | 6.0869 | 6.9852 | 10.4263 | 13.6536 | 17.7996 | 21.5844 | 24.294 | 15.1921
3064 | 24.1515 | 21.4262 | 17.3725 | 11.7142 | 7.637 | 6.0988 | 6.8936 | 10.4235 | 13.6378 | 17.7897 | 21.6764 | 24.5969 | 15.2848
3065 | 23.938 | 21.0178 | 16.8426 | 11.3998 | 7.417 | 6.0412 | 6.8579 | 10.0728 | 13.1859 | 17.4029 | 21.4876 | 24.28 | 14.9953
3066 | 23.938 | 21.0178 | 16.8426 | 11.3998 | 7.417 | 6.0412 | 6.8579 | 10.0728 | 13.1859 | 17.4029 | 21.4876 | 24.28 | 14.9953
3067 | 23.938 | 21.0178 | 16.8426 | 11.3998 | 7.417 | 6.0412 | 6.8579 | 10.0728 | 13.1859 | 17.4029 | 21.4876 | 24.28 | 14.9953
3068 | 23.938 | 21.0178 | 16.8426 | 11.3998 | 7.417 | 6.0412 | 6.8579 | 10.0728 | 13.1859 | 17.4029 | 21.4876 | 24.28 | 14.9953
3070 | 23.8731 | 21.0291 | 16.8323 | 11.3821 | 7.4207 | 6.0012 | 6.8268 | 10.1932 | 13.1883 | 17.439 | 21.4552 | 24.1937 | 14.9862
3071 | 23.8731 | 21.0291 | 16.8323 | 11.3821 | 7.4207 | 6.0012 | 6.8268 | 10.1932 | 13.1883 | 17.439 | 21.4552 | 24.1937 | 14.9862
3072 | 23.8731 | 21.0291 | 16.8323 | 11.3821 | 7.4207 | 6.0012 | 6.8268 | 10.1932 | 13.1883 | 17.439 | 21.4552 | 24.1937 | 14.9862
3073 | 23.8053 | 21.193 | 16.9902 | 11.423 | 7.4443 | 5.9869 | 6.8238 | 10.1403 | 13.2044 | 17.4409 | 21.4281 | 24.216 | 15.008
3074 | 23.8053 | 21.193 | 16.9902 | 11.423 | 7.4443 | 5.9869 | 6.8238 | 10.1403 | 13.2044 | 17.4409 | 21.4281 | 24.216 | 15.008
3075 | 23.8942 | 21.279 | 17.0669 | 11.5025 | 7.453 | 6.0036 | 6.8689 | 10.1067 | 13.283 | 17.484 | 21.3806 | 24.2921 | 15.0512
3076 | 23.8376 | 21.2662 | 16.9682 | 11.4153 | 7.4272 | 5.9918 | 6.7719 | 10.0962 | 13.2634 | 17.4498 | 21.3872 | 24.1271 | 15.0002
3078 | 23.938 | 21.0178 | 16.8426 | 11.3998 | 7.417 | 6.0412 | 6.8579 | 10.0728 | 13.1859 | 17.4029 | 21.4876 | 24.28 | 14.9953
3079 | 23.7347 | 20.9413 | 16.835 | 11.3409 | 7.3531 | 5.9932 | 6.7586 | 10.059 | 13.1314 | 17.2069 | 21.3115 | 24.0663 | 14.8943
3081 | 23.7347 | 20.9413 | 16.835 | 11.3409 | 7.3531 | 5.9932 | 6.7586 | 10.059 | 13.1314 | 17.2069 | 21.3115 | 24.0663 | 14.8943
3082 | 23.8376 | 21.2662 | 16.9682 | 11.4153 | 7.4272 | 5.9918 | 6.7719 | 10.0962 | 13.2634 | 17.4498 | 21.3872 | 24.1271 | 15.0002
3083 | 23.7892 | 21.0916 | 16.9161 | 11.3404 | 7.3774 | 5.9284 | 6.7949 | 10.0695 | 13.1233 | 17.3053 | 21.3113 | 24.1095 | 14.9297
3084 | 23.5885 | 20.7718 | 16.7363 | 11.2675 | 7.2911 | 5.9678 | 6.6691 | 9.892 | 12.9588 | 16.9666 | 21.2924 | 24.016 | 14.7848
3085 | 23.641 | 21.0071 | 16.8746 | 11.3188 | 7.3244 | 5.9227 | 6.6794 | 9.994 | 13.0144 | 17.2114 | 21.3485 | 23.9621 | 14.8582
3086 | 23.7892 | 21.0916 | 16.9161 | 11.3404 | 7.3774 | 5.9284 | 6.7949 | 10.0695 | 13.1233 | 17.3053 | 21.3113 | 24.1095 | 14.9297
3087 | 23.641 | 21.0071 | 16.8746 | 11.3188 | 7.3244 | 5.9227 | 6.6794 | 9.994 | 13.0144 | 17.2114 | 21.3485 | 23.9621 | 14.8582
3088 | 23.641 | 21.0071 | 16.8746 | 11.3188 | 7.3244 | 5.9227 | 6.6794 | 9.994 | 13.0144 | 17.2114 | 21.3485 | 23.9621 | 14.8582
3089 | 23.7634 | 21.1351 | 16.842 | 11.2694 | 7.282 | 5.9165 | 6.5862 | 9.9317 | 13.0377 | 16.9526 | 21.3352 | 23.9824 | 14.8362
3090 | 23.8202 | 21.1949 | 16.9549 | 11.3506 | 7.3824 | 5.9428 | 6.6986 | 10.0478 | 13.2279 | 17.27 | 21.5257 | 24.1092 | 14.9604
3091 | 23.7634 | 21.1351 | 16.842 | 11.2694 | 7.282 | 5.9165 | 6.5862 | 9.9317 | 13.0377 | 16.9526 | 21.3352 | 23.9824 | 14.8362
3093 | 23.5885 | 20.7718 | 16.7363 | 11.2675 | 7.2911 | 5.9678 | 6.6691 | 9.892 | 12.9588 | 16.9666 | 21.2924 | 24.016 | 14.7848
3094 | 23.641 | 21.0071 | 16.8746 | 11.3188 | 7.3244 | 5.9227 | 6.6794 | 9.994 | 13.0144 | 17.2114 | 21.3485 | 23.9621 | 14.8582
3095 | 23.6106 | 20.9934 | 16.7752 | 11.2528 | 7.2773 | 5.892 | 6.606 | 9.9417 | 12.9839 | 16.9983 | 21.2588 | 23.9 | 14.7908
3096 | 23.6633 | 21.0257 | 16.7755 | 11.2298 | 7.2231 | 5.8179 | 6.5446 | 9.8155 | 12.9683 | 16.8501 | 21.0771 | 23.7473 | 14.7282
3097 | 23.4633 | 20.9481 | 16.7125 | 11.1952 | 7.1764 | 5.796 | 6.5631 | 9.6785 | 12.8151 | 16.5702 | 21.1619 | 23.6809 | 14.6468
3099 | 23.6286 | 20.8633 | 16.6779 | 11.2359 | 7.2299 | 5.7456 | 6.4128 | 9.7534 | 12.9207 | 16.7578 | 20.8907 | 23.6241 | 14.6451
3101 | 23.8131 | 20.9469 | 16.7714 | 11.343 | 7.3541 | 6.0277 | 6.7654 | 10.013 | 13.0977 | 17.1652 | 21.3311 | 24.1394 | 14.8973
3102 | 23.8131 | 20.9469 | 16.7714 | 11.343 | 7.3541 | 6.0277 | 6.7654 | 10.013 | 13.0977 | 17.1652 | 21.3311 | 24.1394 | 14.8973
3103 | 23.6207 | 20.8945 | 16.6831 | 11.2067 | 7.2828 | 5.9594 | 6.684 | 9.8901 | 12.8831 | 17.0427 | 21.3052 | 23.9667 | 14.7849
3104 | 23.6207 | 20.8945 | 16.6831 | 11.2067 | 7.2828 | 5.9594 | 6.684 | 9.8901 | 12.8831 | 17.0427 | 21.3052 | 23.9667 | 14.7849
3105 | 23.5885 | 20.7718 | 16.7363 | 11.2675 | 7.2911 | 5.9678 | 6.6691 | 9.892 | 12.9588 | 16.9666 | 21.2924 | 24.016 | 14.7848
3106 | 23.5884 | 20.81 | 16.6808 | 11.1791 | 7.2134 | 5.9289 | 6.6116 | 9.8385 | 12.8462 | 16.8386 | 21.2653 | 23.86 | 14.7217
3107 | 23.5885 | 20.7718 | 16.7363 | 11.2675 | 7.2911 | 5.9678 | 6.6691 | 9.892 | 12.9588 | 16.9666 | 21.2924 | 24.016 | 14.7848
3108 | 23.6207 | 20.8945 | 16.6831 | 11.2067 | 7.2828 | 5.9594 | 6.684 | 9.8901 | 12.8831 | 17.0427 | 21.3052 | 23.9667 | 14.7849
3109 | 23.5712 | 20.7652 | 16.643 | 11.1197 | 7.2417 | 5.8864 | 6.6281 | 9.8249 | 12.7755 | 16.9008 | 21.2357 | 23.8294 | 14.7018
3111 | 23.4814 | 20.7844 | 16.6045 | 11.0911 | 7.2177 | 5.8358 | 6.5962 | 9.7582 | 12.7281 | 16.7344 | 21.154 | 23.7243 | 14.6425
3113 | 23.6111 | 20.8867 | 16.6868 | 11.1655 | 7.1754 | 5.8739 | 6.6122 | 9.8121 | 12.7988 | 16.6871 | 21.2049 | 23.8075 | 14.6935
3114 | 23.4814 | 20.7844 | 16.6045 | 11.0911 | 7.2177 | 5.8358 | 6.5962 | 9.7582 | 12.7281 | 16.7344 | 21.154 | 23.7243 | 14.6425
3115 | 23.5852 | 20.8968 | 16.6372 | 11.1976 | 7.2156 | 5.8415 | 6.5549 | 9.7332 | 12.7001 | 16.5281 | 21.1269 | 23.7612 | 14.6482
3116 | 23.591 | 20.9035 | 16.4746 | 11.1335 | 7.2216 | 5.8599 | 6.5489 | 9.6877 | 12.4531 | 16.4367 | 21.1074 | 23.7017 | 14.5933
3121 | 23.938 | 21.0178 | 16.8426 | 11.3998 | 7.417 | 6.0412 | 6.8579 | 10.0728 | 13.1859 | 17.4029 | 21.4876 | 24.28 | 14.9953
3122 | 23.9382 | 20.9889 | 16.7686 | 11.2813 | 7.3531 | 6.0063 | 6.8225 | 10.0391 | 13.0319 | 17.2504 | 21.5187 | 24.1337 | 14.9277
3123 | 23.9382 | 20.9889 | 16.7686 | 11.2813 | 7.3531 | 6.0063 | 6.8225 | 10.0391 | 13.0319 | 17.2504 | 21.5187 | 24.1337 | 14.9277
3124 | 23.7924 | 20.8881 | 16.738 | 11.2289 | 7.3144 | 5.9386 | 6.7914 | 9.9052 | 12.8949 | 17.0696 | 21.3516 | 23.9095 | 14.8186
3125 | 23.7924 | 20.8881 | 16.738 | 11.2289 | 7.3144 | 5.9386 | 6.7914 | 9.9052 | 12.8949 | 17.0696 | 21.3516 | 23.9095 | 14.8186
3126 | 23.7924 | 20.8881 | 16.738 | 11.2289 | 7.3144 | 5.9386 | 6.7914 | 9.9052 | 12.8949 | 17.0696 | 21.3516 | 23.9095 | 14.8186
3127 | 23.6207 | 20.8945 | 16.6831 | 11.2067 | 7.2828 | 5.9594 | 6.684 | 9.8901 | 12.8831 | 17.0427 | 21.3052 | 23.9667 | 14.7849
3128 | 23.7924 | 20.8881 | 16.738 | 11.2289 | 7.3144 | 5.9386 | 6.7914 | 9.9052 | 12.8949 | 17.0696 | 21.3516 | 23.9095 | 14.8186
3129 | 23.6207 | 20.8945 | 16.6831 | 11.2067 | 7.2828 | 5.9594 | 6.684 | 9.8901 | 12.8831 | 17.0427 | 21.3052 | 23.9667 | 14.7849
3130 | 23.5712 | 20.7652 | 16.643 | 11.1197 | 7.2417 | 5.8864 | 6.6281 | 9.8249 | 12.7755 | 16.9008 | 21.2357 | 23.8294 | 14.7018
3131 | 23.5712 | 20.7652 | 16.643 | 11.1197 | 7.2417 | 5.8864 | 6.6281 | 9.8249 | 12.7755 | 16.9008 | 21.2357 | 23.8294 | 14.7018
3132 | 23.4814 | 20.7844 | 16.6045 | 11.0911 | 7.2177 | 5.8358 | 6.5962 | 9.7582 | 12.7281 | 16.7344 | 21.154 | 23.7243 | 14.6425
3133 | 23.4825 | 20.6921 | 16.5405 | 11.0744 | 7.2746 | 5.8222 | 6.6306 | 9.7327 | 12.7284 | 16.6963 | 21.1961 | 23.7477 | 14.6348
3134 | 23.575 | 20.7946 | 16.4601 | 11.0899 | 7.1983 | 5.7838 | 6.4936 | 9.7359 | 12.6422 | 16.4966 | 21.0425 | 23.6809 | 14.5828
3135 | 23.575 | 20.7946 | 16.4601 | 11.0899 | 7.1983 | 5.7838 | 6.4936 | 9.7359 | 12.6422 | 16.4966 | 21.0425 | 23.6809 | 14.5828
3136 | 23.6784 | 20.902 | 16.4266 | 11.0076 | 7.1703 | 5.7812 | 6.4874 | 9.7033 | 12.6017 | 16.4628 | 20.9484 | 23.6061 | 14.5647
3137 | 23.6784 | 20.902 | 16.4266 | 11.0076 | 7.1703 | 5.7812 | 6.4874 | 9.7033 | 12.6017 | 16.4628 | 20.9484 | 23.6061 | 14.5647
3138 | 23.7493 | 20.9963 | 16.5177 | 11.0025 | 7.1497 | 5.772 | 6.446 | 9.6561 | 12.6017 | 16.4811 | 20.9073 | 23.5546 | 14.5695
3139 | 23.8201 | 20.9769 | 16.4616 | 11.0391 | 7.1617 | 5.6144 | 6.264 | 9.5786 | 12.4655 | 16.4748 | 20.6537 | 23.4949 | 14.5004
3140 | 23.78 | 21.0528 | 16.5196 | 11.0573 | 7.1899 | 5.8576 | 6.4919 | 9.6819 | 12.419 | 16.5679 | 21.1765 | 23.7801 | 14.6312
3141 | 24.0628 | 21.1252 | 16.8637 | 11.3486 | 7.3687 | 6.0131 | 6.8627 | 10.1067 | 13.1488 | 17.5799 | 21.6054 | 24.3963 | 15.0402
3142 | 24.0628 | 21.1252 | 16.8637 | 11.3486 | 7.3687 | 6.0131 | 6.8627 | 10.1067 | 13.1488 | 17.5799 | 21.6054 | 24.3963 | 15.0402
3143 | 24.0628 | 21.1252 | 16.8637 | 11.3486 | 7.3687 | 6.0131 | 6.8627 | 10.1067 | 13.1488 | 17.5799 | 21.6054 | 24.3963 | 15.0402
3144 | 23.9382 | 20.9889 | 16.7686 | 11.2813 | 7.3531 | 6.0063 | 6.8225 | 10.0391 | 13.0319 | 17.2504 | 21.5187 | 24.1337 | 14.9277
3145 | 24.0964 | 21.1327 | 16.8323 | 11.2215 | 7.2853 | 5.9695 | 6.9192 | 9.9705 | 13.0774 | 17.5623 | 21.6472 | 24.2871 | 15.0001
3146 | 23.9382 | 20.9889 | 16.7686 | 11.2813 | 7.3531 | 6.0063 | 6.8225 | 10.0391 | 13.0319 | 17.2504 | 21.5187 | 24.1337 | 14.9277
3147 | 23.7924 | 20.8881 | 16.738 | 11.2289 | 7.3144 | 5.9386 | 6.7914 | 9.9052 | 12.8949 | 17.0696 | 21.3516 | 23.9095 | 14.8186
3148 | 23.8765 | 21.0288 | 16.8158 | 11.1626 | 7.2638 | 5.9098 | 6.8482 | 9.8623 | 13.0185 | 17.2757 | 21.3457 | 24.1202 | 14.8773
3149 | 23.7623 | 20.8211 | 16.713 | 11.0958 | 7.2855 | 5.8967 | 6.7898 | 9.7681 | 12.8506 | 17.0256 | 21.25 | 23.8818 | 14.7617
3150 | 23.5948 | 20.7844 | 16.557 | 11.0529 | 7.3312 | 5.8503 | 6.7472 | 9.7385 | 12.7596 | 16.7631 | 21.1812 | 23.7833 | 14.6786
3151 | 23.6488 | 20.7932 | 16.6931 | 11.1339 | 7.3102 | 5.8887 | 6.7088 | 9.8182 | 12.8176 | 16.9871 | 21.3352 | 23.792 | 14.7439
3152 | 23.5149 | 20.7343 | 16.3718 | 11.0283 | 7.2302 | 5.789 | 6.4998 | 9.6643 | 12.6242 | 16.525 | 21.0315 | 23.5958 | 14.5508
3153 | 23.5149 | 20.7343 | 16.3718 | 11.0283 | 7.2302 | 5.789 | 6.4998 | 9.6643 | 12.6242 | 16.525 | 21.0315 | 23.5958 | 14.5508
3154 | 23.589 | 20.7869 | 16.2448 | 10.9785 | 7.161 | 5.7165 | 6.4466 | 9.5735 | 12.6191 | 16.3976 | 20.8683 | 23.46 | 14.4868
3155 | 23.589 | 20.7869 | 16.2448 | 10.9785 | 7.161 | 5.7165 | 6.4466 | 9.5735 | 12.6191 | 16.3976 | 20.8683 | 23.46 | 14.4868
3156 | 23.4864 | 20.7185 | 16.2241 | 10.9125 | 7.0478 | 5.6927 | 6.568 | 9.5377 | 12.6401 | 16.387 | 20.7733 | 23.1078 | 14.4247
3158 | 23.5128 | 20.6973 | 16.2243 | 10.9325 | 7.1125 | 5.6466 | 6.4963 | 9.5208 | 12.6045 | 16.297 | 20.7376 | 23.2664 | 14.4207
3159 | 23.5671 | 20.5895 | 16.0809 | 10.9303 | 7.1054 | 5.5898 | 6.3017 | 9.5489 | 12.5065 | 16.4905 | 20.906 | 23.1878 | 14.4004
3160 | 23.4012 | 20.4299 | 16.0305 | 10.8566 | 7.037 | 5.5115 | 6.3772 | 9.4363 | 12.5575 | 16.1149 | 20.549 | 22.8662 | 14.264
3161 | 24.0628 | 21.1252 | 16.8637 | 11.3486 | 7.3687 | 6.0131 | 6.8627 | 10.1067 | 13.1488 | 17.5799 | 21.6054 | 24.3963 | 15.0402
3162 | 24.0964 | 21.1327 | 16.8323 | 11.2215 | 7.2853 | 5.9695 | 6.9192 | 9.9705 | 13.0774 | 17.5623 | 21.6472 | 24.2871 | 15.0001
3163 | 24.0964 | 21.1327 | 16.8323 | 11.2215 | 7.2853 | 5.9695 | 6.9192 | 9.9705 | 13.0774 | 17.5623 | 21.6472 | 24.2871 | 15.0001
3165 | 24.0964 | 21.1327 | 16.8323 | 11.2215 | 7.2853 | 5.9695 | 6.9192 | 9.9705 | 13.0774 | 17.5623 | 21.6472 | 24.2871 | 15.0001
3166 | 23.8765 | 21.0288 | 16.8158 | 11.1626 | 7.2638 | 5.9098 | 6.8482 | 9.8623 | 13.0185 | 17.2757 | 21.3457 | 24.1202 | 14.8773
3167 | 24.0282 | 21.1769 | 16.8136 | 11.178 | 7.2902 | 5.9792 | 6.8959 | 9.9052 | 13.2239 | 17.507 | 21.6087 | 24.3846 | 14.9993
3168 | 23.8765 | 21.0288 | 16.8158 | 11.1626 | 7.2638 | 5.9098 | 6.8482 | 9.8623 | 13.0185 | 17.2757 | 21.3457 | 24.1202 | 14.8773
3169 | 24.0282 | 21.1769 | 16.8136 | 11.178 | 7.2902 | 5.9792 | 6.8959 | 9.9052 | 13.2239 | 17.507 | 21.6087 | 24.3846 | 14.9993
3170 | 23.7623 | 20.8211 | 16.713 | 11.0958 | 7.2855 | 5.8967 | 6.7898 | 9.7681 | 12.8506 | 17.0256 | 21.25 | 23.8818 | 14.7617
3171 | 23.8936 | 20.9553 | 16.7215 | 11.1561 | 7.3066 | 5.9696 | 6.8287 | 9.8154 | 13.0205 | 17.1538 | 21.4281 | 24.0691 | 14.8598
3172 | 24.0124 | 21.087 | 16.6984 | 11.1704 | 7.3754 | 6.0481 | 6.9028 | 9.9925 | 13.2242 | 17.3786 | 21.6314 | 24.1328 | 14.9712
3173 | 24.0124 | 21.087 | 16.6984 | 11.1704 | 7.3754 | 6.0481 | 6.9028 | 9.9925 | 13.2242 | 17.3786 | 21.6314 | 24.1328 | 14.9712
3174 | 23.6887 | 20.8585 | 16.614 | 11.0242 | 7.3109 | 5.9303 | 6.7944 | 9.8794 | 12.9371 | 16.86 | 21.2426 | 23.8419 | 14.7485
3175 | 23.8853 | 21.0703 | 16.5771 | 11.0577 | 7.3437 | 6.0662 | 6.8923 | 10.0327 | 13.2624 | 17.3479 | 21.5495 | 24.0648 | 14.9292
3177 | 23.5515 | 20.7817 | 16.5148 | 10.9561 | 7.1871 | 5.9217 | 6.7644 | 9.9386 | 12.9609 | 16.7931 | 21.1497 | 23.6524 | 14.681
3178 | 23.5092 | 20.7839 | 16.4123 | 10.9433 | 7.218 | 5.8872 | 6.7496 | 9.7223 | 12.8184 | 16.5929 | 21.0668 | 23.5344 | 14.6032
3179 | 23.5948 | 20.7844 | 16.557 | 11.0529 | 7.3312 | 5.8503 | 6.7472 | 9.7385 | 12.7596 | 16.7631 | 21.1812 | 23.7833 | 14.6786
3180 | 23.4561 | 20.7059 | 16.4049 | 10.9819 | 7.2741 | 5.8209 | 6.6191 | 9.6478 | 12.6643 | 16.5106 | 21.0524 | 23.5241 | 14.5552
3181 | 24.0628 | 21.1252 | 16.8637 | 11.3486 | 7.3687 | 6.0131 | 6.8627 | 10.1067 | 13.1488 | 17.5799 | 21.6054 | 24.3963 | 15.0402
3182 | 24.0628 | 21.1252 | 16.8637 | 11.3486 | 7.3687 | 6.0131 | 6.8627 | 10.1067 | 13.1488 | 17.5799 | 21.6054 | 24.3963 | 15.0402
3183 | 24.0628 | 21.1252 | 16.8637 | 11.3486 | 7.3687 | 6.0131 | 6.8627 | 10.1067 | 13.1488 | 17.5799 | 21.6054 | 24.3963 | 15.0402
3184 | 24.1769 | 21.1389 | 16.9399 | 11.2498 | 7.3172 | 5.9862 | 6.9393 | 10.1339 | 13.2114 | 17.8992 | 21.7665 | 24.6141 | 15.1144
3185 | 24.1769 | 21.1389 | 16.9399 | 11.2498 | 7.3172 | 5.9862 | 6.9393 | 10.1339 | 13.2114 | 17.8992 | 21.7665 | 24.6141 | 15.1144
3186 | 24.1769 | 21.1389 | 16.9399 | 11.2498 | 7.3172 | 5.9862 | 6.9393 | 10.1339 | 13.2114 | 17.8992 | 21.7665 | 24.6141 | 15.1144
3187 | 24.1769 | 21.1389 | 16.9399 | 11.2498 | 7.3172 | 5.9862 | 6.9393 | 10.1339 | 13.2114 | 17.8992 | 21.7665 | 24.6141 | 15.1144
3188 | 24.2121 | 21.1878 | 17.0635 | 11.2374 | 7.2877 | 6.0003 | 7.0183 | 10.1202 | 13.3329 | 18.1629 | 22.0542 | 24.8223 | 15.2083
3189 | 24.131 | 21.2421 | 16.9291 | 11.1826 | 7.275 | 6.0163 | 6.9907 | 9.9796 | 13.2829 | 17.9216 | 21.8328 | 24.6064 | 15.1158
3190 | 24.131 | 21.2421 | 16.9291 | 11.1826 | 7.275 | 6.0163 | 6.9907 | 9.9796 | 13.2829 | 17.9216 | 21.8328 | 24.6064 | 15.1158
3191 | 24.2121 | 21.1878 | 17.0635 | 11.2374 | 7.2877 | 6.0003 | 7.0183 | 10.1202 | 13.3329 | 18.1629 | 22.0542 | 24.8223 | 15.2083
3192 | 24.131 | 21.2421 | 16.9291 | 11.1826 | 7.275 | 6.0163 | 6.9907 | 9.9796 | 13.2829 | 17.9216 | 21.8328 | 24.6064 | 15.1158
3193 | 24.195 | 21.1677 | 16.9699 | 11.2583 | 7.2757 | 6.034 | 7.0541 | 10.157 | 13.4787 | 18.2182 | 22.0182 | 24.7837 | 15.2175
3194 | 24.0804 | 21.2072 | 16.8071 | 11.1556 | 7.2956 | 6.056 | 7.0198 | 10.0395 | 13.4144 | 17.8027 | 21.857 | 24.5952 | 15.1109
3195 | 24.0804 | 21.2072 | 16.8071 | 11.1556 | 7.2956 | 6.056 | 7.0198 | 10.0395 | 13.4144 | 17.8027 | 21.857 | 24.5952 | 15.1109
3196 | 24.043 | 21.0457 | 16.8686 | 11.1892 | 7.2782 | 5.9908 | 6.9708 | 10.2847 | 13.495 | 18.0572 | 22.0839 | 24.714 | 15.1684
3197 | 24.0752 | 21.1695 | 16.7307 | 11.1833 | 7.3516 | 6.0606 | 6.9494 | 10.1777 | 13.4192 | 17.5973 | 21.8632 | 24.4918 | 15.0891
3198 | 24.1207 | 21.1692 | 16.8612 | 11.0976 | 7.3239 | 6.0547 | 6.9081 | 10.3735 | 13.4049 | 17.7866 | 22.0401 | 24.5184 | 15.1382
3199 | 24.0644 | 21.0735 | 16.8497 | 11.0473 | 7.2848 | 6.0065 | 6.9532 | 10.325 | 13.4521 | 17.8653 | 21.969 | 24.4331 | 15.1103
3200 | 24.0644 | 21.0735 | 16.8497 | 11.0473 | 7.2848 | 6.0065 | 6.9532 | 10.325 | 13.4521 | 17.8653 | 21.969 | 24.4331 | 15.1103
3201 | 24.1207 | 21.1692 | 16.8612 | 11.0976 | 7.3239 | 6.0547 | 6.9081 | 10.3735 | 13.4049 | 17.7866 | 22.0401 | 24.5184 | 15.1382
3202 | 24.0282 | 21.1769 | 16.8136 | 11.178 | 7.2902 | 5.9792 | 6.8959 | 9.9052 | 13.2239 | 17.507 | 21.6087 | 24.3846 | 14.9993
3204 | 24.0964 | 21.1327 | 16.8323 | 11.2215 | 7.2853 | 5.9695 | 6.9192 | 9.9705 | 13.0774 | 17.5623 | 21.6472 | 24.2871 | 15.0001
3205 | 24.0437 | 21.1551 | 16.9355 | 11.3803 | 7.2917 | 6.0476 | 6.9356 | 10.2355 | 13.2996 | 17.784 | 21.706 | 24.3783 | 15.0994
3206 | 24.0437 | 21.1551 | 16.9355 | 11.3803 | 7.2917 | 6.0476 | 6.9356 | 10.2355 | 13.2996 | 17.784 | 21.706 | 24.3783 | 15.0994
3207 | 23.985 | 21.0146 | 17.1013 | 11.4161 | 7.345 | 6.1022 | 7.0274 | 10.2412 | 13.406 | 17.7317 | 21.6997 | 24.1034 | 15.0978
3211 | 23.8007 | 20.8798 | 16.9417 | 11.4079 | 7.6622 | 6.2615 | 7.2242 | 10.452 | 13.8588 | 17.8445 | 21.6712 | 23.985 | 15.1658
3212 | 23.9476 | 21.0258 | 17.0651 | 11.3409 | 7.4809 | 6.1536 | 7.1226 | 10.5023 | 13.7867 | 18.1118 | 21.6112 | 23.9152 | 15.172
3214 | 23.9889 | 20.9064 | 16.816 | 11.3304 | 7.4632 | 6.2587 | 7.2034 | 10.3927 | 13.8372 | 18.0118 | 21.4508 | 23.9413 | 15.1334
3215 | 23.9889 | 20.9064 | 16.816 | 11.3304 | 7.4632 | 6.2587 | 7.2034 | 10.3927 | 13.8372 | 18.0118 | 21.4508 | 23.9413 | 15.1334
3216 | 24.1171 | 21.2685 | 16.7407 | 11.3405 | 7.5596 | 6.2458 | 7.141 | 10.2777 | 14.0083 | 17.7941 | 21.7241 | 24.2967 | 15.2095
3217 | 24.1171 | 21.2685 | 16.7407 | 11.3405 | 7.5596 | 6.2458 | 7.141 | 10.2777 | 14.0083 | 17.7941 | 21.7241 | 24.2967 | 15.2095
3218 | 23.874 | 21.0172 | 16.8257 | 11.4455 | 7.4698 | 6.2154 | 7.1384 | 10.355 | 13.977 | 17.8809 | 21.3234 | 23.8081 | 15.1109
3219 | 23.874 | 21.0172 | 16.8257 | 11.4455 | 7.4698 | 6.2154 | 7.1384 | 10.355 | 13.977 | 17.8809 | 21.3234 | 23.8081 | 15.1109
3220 | 23.874 | 21.0172 | 16.8257 | 11.4455 | 7.4698 | 6.2154 | 7.1384 | 10.355 | 13.977 | 17.8809 | 21.3234 | 23.8081 | 15.1109
3221 | 24.0266 | 21.1984 | 16.5678 | 11.4716 | 7.5906 | 6.2702 | 7.1598 | 10.3983 | 13.7303 | 17.8855 | 21.6171 | 24.2733 | 15.1825
3222 | 24.318 | 21.0658 | 16.9035 | 11.3201 | 7.3788 | 6.0897 | 7.0819 | 10.2755 | 13.6199 | 17.5369 | 21.7948 | 24.6951 | 15.1733
3223 | 24.203 | 21.1158 | 17.3551 | 11.6149 | 7.4913 | 6.1044 | 7.1255 | 10.3507 | 14.0714 | 17.5497 | 21.8084 | 24.458 | 15.2707
3224 | 23.9915 | 20.8508 | 16.7701 | 11.2874 | 7.3901 | 6.1256 | 7.011 | 10.0822 | 13.6139 | 17.5793 | 21.5866 | 24.3752 | 15.0553
3225 | 24.4655 | 21.3599 | 17.2368 | 11.3629 | 7.2542 | 5.9818 | 7.0987 | 10.3749 | 13.8334 | 17.8537 | 22.0184 | 24.7619 | 15.3002
3226 | 24.4947 | 21.3187 | 16.9917 | 11.2221 | 7.2386 | 6.0459 | 7.1102 | 10.2228 | 13.505 | 17.7826 | 22.0312 | 24.7592 | 15.2269
3227 | 24.3424 | 21.1992 | 16.8049 | 11.2253 | 7.3733 | 6.1951 | 7.0705 | 10.2655 | 13.7125 | 17.7242 | 21.9426 | 24.6745 | 15.2108
3228 | 24.3715 | 21.3718 | 16.6735 | 11.2312 | 7.2269 | 6.1433 | 6.9724 | 10.3271 | 13.949 | 18.0582 | 22.1365 | 24.3934 | 15.2379
3230 | 24.0261 | 21.1453 | 16.5815 | 11.2709 | 7.1814 | 6.0478 | 6.9404 | 10.3169 | 13.8632 | 17.9134 | 22.0161 | 24.1813 | 15.1237
3231 | 23.7146 | 20.6501 | 16.1307 | 11.1113 | 7.186 | 5.8765 | 6.7574 | 10.1884 | 13.7751 | 17.8323 | 21.7158 | 23.8986 | 14.9031
3232 | 23.2104 | 20.184 | 15.9356 | 10.9551 | 6.914 | 5.5534 | 6.4781 | 9.9437 | 13.847 | 17.6514 | 21.2169 | 23.4948 | 14.6154
3233 | 22.0867 | 19.5504 | 15.1623 | 10.4361 | 6.4893 | 5.3238 | 6.2319 | 9.557 | 13.2419 | 16.8827 | 20.3552 | 22.5644 | 13.9901
3235 | 24.3212 | 21.2316 | 16.5983 | 11.2796 | 7.2299 | 5.9205 | 6.757 | 9.9479 | 13.5075 | 17.7506 | 21.8713 | 24.5867 | 15.0835
3236 | 23.969 | 20.9019 | 16.0748 | 11.0607 | 6.9608 | 5.5998 | 6.5481 | 9.7728 | 12.9839 | 17.3067 | 21.9498 | 24.2642 | 14.7827
3237 | 22.7132 | 19.7389 | 15.0391 | 10.446 | 6.6012 | 5.3325 | 6.2819 | 9.379 | 12.3004 | 16.6041 | 20.8633 | 22.9649 | 14.0221
3238 | 21.8984 | 19.5394 | 14.7355 | 10.2402 | 6.4778 | 5.2191 | 6.1038 | 9.3039 | 12.6968 | 16.5164 | 20.2374 | 22.5215 | 13.7909
3239 | 23.7661 | 20.7438 | 15.9375 | 10.9186 | 6.9044 | 5.5148 | 6.5729 | 9.6617 | 12.9672 | 17.2521 | 21.5732 | 24.1131 | 14.6605
3240 | 24.3595 | 21.402 | 16.6617 | 11.4544 | 7.3794 | 6.1017 | 6.9788 | 10.115 | 13.4722 | 17.7781 | 21.8592 | 24.4693 | 15.1693
3241 | 24.5965 | 21.5901 | 16.7563 | 11.5424 | 7.4888 | 6.143 | 6.9431 | 10.1013 | 13.3761 | 17.7877 | 21.9705 | 24.6476 | 15.2453
3242 | 24.7608 | 21.5723 | 16.8218 | 11.7101 | 7.6176 | 6.2139 | 7.0399 | 10.1585 | 13.8096 | 17.9946 | 21.9995 | 24.8162 | 15.3762
3243 | 24.5917 | 21.3905 | 16.3685 | 11.2519 | 7.1008 | 5.7336 | 6.6415 | 9.8834 | 13.1206 | 17.4635 | 21.9839 | 24.6552 | 15.0154
3249 | 24.5666 | 21.7216 | 16.5903 | 11.3308 | 7.1129 | 5.7616 | 6.7332 | 9.9614 | 13.0717 | 17.4103 | 21.9797 | 24.6022 | 15.0702
3250 | 24.5265 | 21.3334 | 16.6167 | 11.4425 | 7.2675 | 5.8547 | 6.7804 | 10.0279 | 13.37 | 17.5905 | 21.932 | 24.8199 | 15.1302
3251 | 24.7577 | 21.7332 | 17.0276 | 11.8292 | 7.6438 | 6.2466 | 7.0993 | 10.1137 | 13.4812 | 17.7735 | 21.7717 | 24.8387 | 15.3597
3254 | 24.8905 | 21.6761 | 16.7157 | 11.6164 | 7.3007 | 5.8639 | 6.9213 | 10.1142 | 13.468 | 17.707 | 21.8304 | 24.7983 | 15.2419
3260 | 24.7893 | 21.8929 | 16.9239 | 11.6015 | 7.3848 | 6.0006 | 7.0161 | 10.1066 | 13.6214 | 17.7664 | 21.8812 | 24.7257 | 15.3092
3264 | 24.6448 | 21.323 | 16.5567 | 11.3669 | 7.217 | 5.9506 | 6.9525 | 9.9262 | 13.2675 | 17.3541 | 21.4691 | 23.9854 | 15.0012
3265 | 24.4622 | 21.2919 | 16.468 | 11.3048 | 7.1819 | 5.9343 | 6.9467 | 9.9545 | 13.2172 | 17.4622 | 21.5946 | 24.1919 | 15.0008
3266 | 24.2383 | 21.1615 | 16.3077 | 11.1229 | 7.0198 | 5.7303 | 6.7969 | 9.819 | 13.1339 | 17.2049 | 21.5582 | 23.9646 | 14.8382
3267 | 24.1551 | 20.9537 | 16.2233 | 10.965 | 6.9489 | 5.7804 | 6.6806 | 9.8051 | 12.9938 | 17.2348 | 21.4968 | 23.7141 | 14.746
3268 | 24.3374 | 21.3441 | 16.3431 | 10.9066 | 6.84 | 5.7459 | 6.7379 | 9.9454 | 13.0921 | 17.5743 | 21.8763 | 24.1715 | 14.9095
3269 | 23.6895 | 20.7262 | 15.7694 | 10.6183 | 6.7074 | 5.5294 | 6.4619 | 9.6939 | 13.1526 | 17.2956 | 21.4434 | 23.7651 | 14.5711
3270 | 24.5294 | 21.4164 | 16.5064 | 10.8042 | 6.7017 | 5.6112 | 6.6288 | 9.8556 | 13.2373 | 18.2217 | 22.1083 | 24.3221 | 14.9953
3272 | 24.674 | 21.914 | 16.8872 | 11.5598 | 7.5672 | 6.2326 | 7.1544 | 10.1784 | 13.5842 | 17.5159 | 21.6195 | 24.6553 | 15.2952
3273 | 24.7639 | 21.5493 | 16.7106 | 11.5318 | 7.3773 | 6.1201 | 7.0468 | 10.0209 | 13.6133 | 17.4925 | 21.7445 | 24.6975 | 15.2224
3274 | 24.7944 | 21.7594 | 16.9216 | 11.654 | 7.6178 | 6.1969 | 7.1627 | 10.3609 | 13.7228 | 17.6671 | 21.8022 | 24.6465 | 15.3589
3275 | 24.3423 | 21.4183 | 16.6795 | 11.1603 | 7.0845 | 5.9123 | 6.965 | 10.0306 | 13.3826 | 17.5393 | 21.8109 | 24.3755 | 15.0584
3276 | 24.511 | 21.5033 | 16.5455 | 11.3556 | 7.3979 | 6.0906 | 7.0386 | 10.3004 | 13.4553 | 17.4862 | 21.623 | 24.2675 | 15.1312
3277 | 24.6676 | 21.624 | 16.7148 | 11.0261 | 6.9123 | 5.8027 | 6.8266 | 9.9271 | 13.3155 | 17.938 | 22.3877 | 24.7591 | 15.1585
3278 | 24.4675 | 21.3018 | 16.5026 | 11.21 | 7.1038 | 5.9813 | 6.9459 | 9.9817 | 13.2327 | 17.3556 | 21.5874 | 24.1182 | 14.9824
3280 | 24.526 | 21.5825 | 16.6854 | 11.138 | 7.053 | 5.9014 | 6.9044 | 9.9709 | 13.3224 | 17.7016 | 21.9521 | 24.4963 | 15.1028
3281 | 24.3375 | 21.2808 | 16.3945 | 11.3209 | 7.1762 | 5.9862 | 7.0697 | 9.9673 | 13.2207 | 17.2132 | 21.5663 | 24.1903 | 14.977
3282 | 24.3403 | 21.4827 | 16.6962 | 11.1892 | 7.1224 | 5.9069 | 6.9369 | 10.0262 | 13.3625 | 17.5479 | 21.8469 | 24.3759 | 15.0695
3283 | 24.3697 | 21.3677 | 16.5749 | 11.2338 | 7.2204 | 5.9621 | 6.9288 | 10.0876 | 13.5154 | 17.5394 | 21.4485 | 24.1319 | 15.0317
3284 | 24.3814 | 21.71 | 16.9382 | 11.2843 | 7.1769 | 5.86 | 6.8212 | 10.1417 | 13.7299 | 18.1841 | 22.1429 | 24.5846 | 15.2463
3285 | 23.8856 | 21.3383 | 16.3473 | 11.2124 | 7.2312 | 5.9668 | 6.8593 | 10.2075 | 13.5151 | 17.6825 | 21.8053 | 23.9654 | 15.0014
3286 | 24.4951 | 21.4487 | 16.2859 | 11.389 | 7.2773 | 5.9894 | 6.8547 | 10.1825 | 13.4728 | 17.5122 | 21.6145 | 24.0023 | 15.0437
3287 | 24.494 | 21.5074 | 16.4611 | 11.459 | 7.3492 | 6.04 | 6.9505 | 10.2367 | 13.5593 | 17.3853 | 21.5988 | 24.0339 | 15.0896
3289 | 25.008 | 21.9769 | 16.8158 | 11.5877 | 7.4516 | 6.058 | 6.9528 | 10.3734 | 13.4855 | 17.5198 | 21.8738 | 24.5278 | 15.3026
3292 | 24.7211 | 21.7825 | 16.6213 | 11.2764 | 7.2878 | 6.0935 | 6.9628 | 10.2921 | 13.563 | 17.7818 | 22.1478 | 24.4649 | 15.2496
3293 | 25.2266 | 22.3439 | 17.2991 | 11.815 | 7.6892 | 6.1986 | 7.015 | 10.3418 | 13.9113 | 17.8224 | 22.2597 | 25.1995 | 15.5935
3294 | 25.101 | 22.234 | 17.2229 | 11.678 | 7.4453 | 5.9512 | 6.7757 | 10.2451 | 13.7789 | 17.8829 | 21.9659 | 24.8027 | 15.4236
3300 | 25.1261 | 22.2434 | 17.0143 | 11.7048 | 7.4642 | 6.0304 | 6.822 | 10.1744 | 13.7257 | 17.7257 | 22.1046 | 24.7535 | 15.4074
3301 | 24.9843 | 22.0684 | 17.0322 | 11.7833 | 7.5387 | 6.1082 | 6.8859 | 10.3008 | 13.6723 | 17.6212 | 22.0648 | 24.6801 | 15.395
3302 | 25.1209 | 22.2141 | 16.8786 | 11.5883 | 7.4025 | 5.9873 | 6.9163 | 10.3352 | 13.5983 | 17.9559 | 22.2631 | 24.7647 | 15.4188
3303 | 24.6015 | 21.6809 | 16.4468 | 11.4279 | 7.3298 | 6.0657 | 6.8774 | 10.2143 | 13.453 | 17.602 | 22.0221 | 24.4018 | 15.1769
3304 | 23.9315 | 21.1517 | 15.9748 | 11.1072 | 7.3032 | 6.0372 | 6.8057 | 10.1946 | 13.3134 | 17.3629 | 21.585 | 23.8358 | 14.8836
3305 | 23.7225 | 20.9363 | 16.0577 | 11.1056 | 7.2623 | 6.045 | 6.7829 | 10.0988 | 13.7205 | 17.8735 | 21.8614 | 23.6382 | 14.9254
3309 | 24.49 | 21.4042 | 16.2359 | 11.2572 | 7.2813 | 6.0591 | 6.7808 | 10.1543 | 13.3341 | 17.3307 | 21.6502 | 24.1233 | 15.0084
3310 | 25.3991 | 22.4875 | 17.2004 | 11.6987 | 7.475 | 6.1127 | 6.8729 | 10.3243 | 13.6394 | 17.9124 | 22.6118 | 25.1897 | 15.577
3311 | 25.3715 | 22.5653 | 16.9145 | 11.611 | 7.3863 | 6.1551 | 7.0122 | 10.2654 | 13.5395 | 17.9228 | 22.5776 | 24.9991 | 15.5267
3312 | 25.4987 | 22.7934 | 17.2328 | 11.7639 | 7.6155 | 6.1969 | 6.9883 | 10.3199 | 13.5747 | 18.0472 | 22.516 | 25.2829 | 15.6525
3314 | 26.0669 | 22.8988 | 17.9851 | 12.3473 | 7.7774 | 6.1841 | 6.8849 | 10.3741 | 13.9655 | 18.3376 | 22.7671 | 25.5004 | 15.9241
3315 | 26.2006 | 23.1402 | 17.8047 | 12.0068 | 7.6753 | 6.1706 | 6.8402 | 10.3844 | 13.9326 | 18.2377 | 22.7894 | 25.6937 | 15.9064
3317 | 26.3991 | 23.4659 | 18.2679 | 12.3859 | 7.9613 | 6.3546 | 7.1469 | 10.617 | 13.935 | 18.7491 | 23.4115 | 26.0325 | 16.2272
3318 | 26.7115 | 23.7787 | 18.665 | 12.6823 | 8.1326 | 6.5392 | 7.3046 | 10.6018 | 14.2357 | 18.9538 | 23.8341 | 26.4075 | 16.4872
3319 | 26.5981 | 23.9501 | 18.7566 | 12.726 | 8.2671 | 6.6014 | 7.4216 | 10.6586 | 14.0999 | 19.0438 | 23.6712 | 26.4002 | 16.5162
3321 | 24.4442 | 21.5752 | 16.8158 | 11.6915 | 7.7444 | 6.2827 | 7.167 | 10.307 | 13.6591 | 17.8075 | 21.7798 | 24.6588 | 15.3277
3324 | 24.6579 | 21.9252 | 17.0993 | 11.8396 | 7.631 | 6.3173 | 7.1184 | 10.2246 | 13.5599 | 17.5629 | 22.0205 | 24.7129 | 15.3891
3325 | 24.5799 | 22.0399 | 16.9635 | 11.7036 | 7.6463 | 6.2653 | 7.0185 | 10.1666 | 13.6143 | 17.4816 | 21.8298 | 24.7966 | 15.3422
3328 | 24.0039 | 21.3713 | 16.7033 | 11.5898 | 7.58 | 6.3013 | 7.1669 | 10.4146 | 13.8347 | 17.7466 | 21.5446 | 24.2649 | 15.2102
3329 | 24.1159 | 21.415 | 16.6755 | 11.6499 | 7.6044 | 6.2541 | 7.0931 | 10.2833 | 13.787 | 17.5913 | 21.398 | 24.2691 | 15.1781
3330 | 24.219 | 21.4548 | 16.918 | 11.6407 | 7.6126 | 6.1595 | 6.9856 | 10.1846 | 13.6205 | 17.4649 | 21.4041 | 24.5878 | 15.1877
3331 | 23.5106 | 20.7113 | 16.4086 | 11.4817 | 7.5512 | 6.2773 | 7.0483 | 10.3236 | 13.8027 | 17.6751 | 21.1152 | 23.8692 | 14.9812
3332 | 23.8007 | 21.1058 | 16.4924 | 11.6123 | 7.5926 | 6.2311 | 7.1002 | 10.3907 | 13.9072 | 17.6454 | 21.1868 | 24.111 | 15.098
3333 | 24.0746 | 21.3382 | 16.6801 | 11.5473 | 7.5772 | 6.1835 | 7.0637 | 10.3735 | 13.8943 | 17.4696 | 21.2812 | 24.3589 | 15.1535
3334 | 23.9579 | 21.1752 | 16.8017 | 11.6939 | 7.5752 | 6.0541 | 6.8896 | 10.2616 | 13.7367 | 17.4626 | 21.5777 | 24.39 | 15.1313
3335 | 23.4312 | 20.8076 | 16.8147 | 11.5088 | 7.665 | 6.3341 | 7.145 | 10.4956 | 13.7789 | 17.7604 | 21.3889 | 23.8595 | 15.0825
3337 | 23.4857 | 20.6978 | 16.6837 | 11.5037 | 7.745 | 6.2215 | 7.0834 | 10.446 | 13.8208 | 17.8381 | 21.3113 | 23.857 | 15.0578
3338 | 23.4649 | 20.803 | 16.798 | 11.5229 | 7.6973 | 6.2774 | 7.2015 | 10.4934 | 13.8682 | 17.7131 | 21.3182 | 23.8463 | 15.0837
3340 | 23.6238 | 20.979 | 16.8454 | 11.6125 | 7.8031 | 6.4182 | 7.2654 | 10.6302 | 14.074 | 18.0177 | 21.4728 | 24.0187 | 15.2301
3341 | 23.5779 | 20.6337 | 16.7952 | 11.5785 | 7.5787 | 5.7183 | 6.7264 | 10.3403 | 14.174 | 17.877 | 21.5512 | 24.0867 | 15.0532
3342 | 24.0048 | 21.3755 | 16.9953 | 11.8017 | 7.7055 | 6.0901 | 7.022 | 10.4046 | 14.1445 | 17.9036 | 21.4758 | 24.5099 | 15.2861
3345 | 24.2053 | 21.5078 | 17.1564 | 11.7534 | 7.4307 | 5.5287 | 6.5106 | 10.0115 | 13.7975 | 17.8257 | 21.6447 | 24.5966 | 15.1641
3350 | 24.8992 | 21.966 | 17.5508 | 11.9224 | 7.5486 | 5.6332 | 6.5414 | 10.1036 | 13.5275 | 17.8545 | 21.7636 | 25.3472 | 15.3882
3351 | 24.7907 | 22.3193 | 17.4554 | 11.8684 | 7.7272 | 6.364 | 7.176 | 10.319 | 13.6421 | 17.7612 | 22.1151 | 25.0661 | 15.5504
3352 | 26.1651 | 23.2584 | 18.6097 | 12.5357 | 7.9781 | 6.0113 | 6.8559 | 10.492 | 14.1802 | 18.5034 | 23.2065 | 26.6799 | 16.2063
3355 | 25.5207 | 22.6643 | 18.1255 | 12.2108 | 7.773 | 5.8013 | 6.6272 | 10.4054 | 13.8141 | 18.229 | 22.454 | 26.0317 | 15.8048
3356 | 24.7309 | 22.0418 | 17.5333 | 11.8734 | 7.5159 | 5.7132 | 6.6112 | 10.1702 | 13.6372 | 17.905 | 21.7843 | 25.1999 | 15.393
3357 | 24.5451 | 21.8333 | 17.1615 | 11.7011 | 7.4289 | 5.7509 | 6.6205 | 10.0585 | 13.431 | 17.6708 | 21.7143 | 24.8307 | 15.2289
3360 | 24.3397 | 21.8648 | 16.8896 | 11.8191 | 7.5729 | 6.0907 | 6.9335 | 10.0827 | 13.6601 | 17.6652 | 21.5335 | 24.7927 | 15.2704
3361 | 24.9435 | 22.2606 | 17.4119 | 11.9597 | 7.8013 | 6.2428 | 6.9837 | 10.2437 | 13.5432 | 17.811 | 22.1095 | 24.9826 | 15.5245
3363 | 25.5895 | 22.569 | 18.2787 | 12.3372 | 7.7896 | 5.7378 | 6.6477 | 10.2541 | 13.8139 | 18.3852 | 22.6693 | 26.0595 | 15.8443
3364 | 26.2476 | 23.1438 | 18.7236 | 12.6618 | 8.0488 | 5.9137 | 6.7846 | 10.3196 | 14.0642 | 18.7194 | 23.2096 | 26.8458 | 16.2235
3370 | 26.3388 | 23.2832 | 18.8916 | 12.8017 | 8.2265 | 6.1849 | 6.9202 | 10.5549 | 14.3866 | 18.9739 | 23.4388 | 26.9352 | 16.4114
3371 | 26.568 | 23.5933 | 19.4814 | 13.2133 | 8.6127 | 6.4082 | 7.2654 | 10.704 | 14.5515 | 19.2927 | 24.0198 | 27.2784 | 16.7491
3373 | 25.7927 | 22.5651 | 18.2888 | 12.3229 | 7.8344 | 6.0109 | 6.8222 | 10.4927 | 14.2252 | 18.4746 | 22.9011 | 26.0596 | 15.9825
3374 | 26.7992 | 23.5862 | 19.158 | 12.9474 | 8.3794 | 6.414 | 7.1523 | 10.8065 | 14.6861 | 19.4538 | 24.089 | 27.278 | 16.7292
3375 | 26.2482 | 22.9905 | 18.6035 | 12.5433 | 8.0016 | 6.0889 | 6.8133 | 10.4391 | 14.0668 | 18.7135 | 23.398 | 26.2456 | 16.1794
3377 | 26.1243 | 23.1972 | 18.5886 | 12.5707 | 8.0717 | 6.3035 | 7.0245 | 10.6054 | 14.4595 | 18.8927 | 23.506 | 26.4187 | 16.3136
3378 | 25.6216 | 23.0201 | 17.9958 | 12.2213 | 7.9798 | 6.177 | 6.9945 | 10.4111 | 14.0592 | 18.3173 | 22.8436 | 25.6753 | 15.943
3379 | 25.2829 | 22.4711 | 17.4362 | 11.9502 | 7.7568 | 6.1616 | 6.9199 | 10.2516 | 13.9884 | 17.9938 | 22.3625 | 25.1104 | 15.6404
3380 | 26.8963 | 23.5323 | 19.3887 | 12.9927 | 8.5976 | 6.559 | 7.2652 | 10.9023 | 14.8169 | 19.8542 | 24.3212 | 27.4192 | 16.8788
3381 | 26.337 | 22.9911 | 18.7943 | 12.6998 | 7.9335 | 6.0294 | 6.6891 | 10.3518 | 14.1918 | 18.8645 | 23.4462 | 26.4312 | 16.23
3384 | 26.9234 | 23.6653 | 19.6317 | 13.3662 | 8.8668 | 6.717 | 7.3762 | 10.8512 | 14.9778 | 19.8632 | 24.38 | 27.4482 | 17.0056
3385 | 27.1047 | 24.0489 | 19.8468 | 13.5803 | 8.9534 | 6.8678 | 7.492 | 10.9118 | 14.6602 | 19.8866 | 24.8561 | 27.5692 | 17.1481
3387 | 27.2231 | 24.0137 | 20.3321 | 14.1055 | 9.4421 | 7.1845 | 7.8477 | 11.2645 | 15.1723 | 20.2529 | 24.7731 | 27.8186 | 17.4525
3388 | 27.1856 | 24.2168 | 20.1899 | 14.0234 | 9.4144 | 7.1958 | 7.8211 | 11.1483 | 14.8293 | 20.1452 | 24.7678 | 27.6149 | 17.3794
3390 | 27.1317 | 24.0611 | 20.0319 | 13.9446 | 9.3705 | 7.2792 | 7.9176 | 11.164 | 14.8278 | 20.0199 | 24.7293 | 27.6321 | 17.3425
3391 | 27.4581 | 24.1493 | 20.4111 | 14.5262 | 9.8528 | 7.742 | 8.3664 | 11.7858 | 15.6473 | 20.6915 | 24.9016 | 27.7742 | 17.7755
3392 | 27.3704 | 24.2821 | 20.3467 | 14.4174 | 9.6301 | 7.4863 | 8.1333 | 11.473 | 15.1648 | 20.3112 | 24.673 | 27.8191 | 17.5923
3393 | 27.3318 | 24.2724 | 20.414 | 14.4857 | 9.6932 | 7.5992 | 8.1503 | 11.6228 | 15.4734 | 20.5956 | 24.7827 | 27.7375 | 17.6799
3395 | 27.7011 | 24.3083 | 20.7592 | 14.6856 | 10.0603 | 7.9193 | 8.547 | 12.0779 | 15.886 | 21.0665 | 24.9988 | 27.8221 | 17.986
3396 | 27.7081 | 24.0256 | 20.7357 | 14.7072 | 10.0267 | 7.9176 | 8.5558 | 12.1284 | 15.89 | 21.0872 | 25.0723 | 27.944 | 17.9832
3400 | 27.0665 | 24.0888 | 19.8747 | 13.7931 | 9.1968 | 7.2362 | 7.7924 | 11.1603 | 14.7771 | 19.7234 | 24.4972 | 27.41 | 17.2181
3401 | 27.0347 | 24.0827 | 19.7903 | 13.7544 | 9.0456 | 7.1353 | 7.7148 | 11.0198 | 14.8235 | 19.701 | 24.4335 | 27.2028 | 17.1449
3407 | 26.4943 | 23.6358 | 18.5288 | 12.702 | 8.1316 | 6.4137 | 7.1026 | 10.5178 | 14.1232 | 18.8052 | 23.6045 | 26.3046 | 16.3637
3409 | 26.8429 | 23.8775 | 19.1276 | 13.1698 | 8.745 | 6.8444 | 7.4941 | 10.9064 | 14.5852 | 19.4708 | 24.2797 | 26.914 | 16.8548
3412 | 26.8007 | 23.5808 | 19.1489 | 13.219 | 8.6937 | 6.8807 | 7.552 | 10.9785 | 14.5225 | 19.2283 | 24.0469 | 26.8499 | 16.7918
3413 | 26.8448 | 23.8755 | 18.9855 | 13.1138 | 8.6355 | 6.9753 | 7.5886 | 10.7722 | 14.3569 | 19.3079 | 24.0662 | 26.6651 | 16.7656
3414 | 27.2397 | 24.3381 | 20.1468 | 14.1202 | 9.3712 | 7.3991 | 8.0727 | 11.4734 | 15.2369 | 20.2075 | 24.5827 | 27.6032 | 17.4826
3418 | 27.3238 | 24.4109 | 20.2526 | 14.0687 | 9.4635 | 7.4583 | 8.2447 | 11.5542 | 15.378 | 20.3595 | 24.8246 | 27.4949 | 17.5695
3419 | 27.089 | 24.1743 | 19.8619 | 13.7404 | 9.1458 | 7.1982 | 7.9167 | 11.2114 | 14.8717 | 19.8897 | 24.6286 | 27.1956 | 17.2436
3420 | 27.3115 | 23.9586 | 19.916 | 14.0321 | 9.3957 | 7.3849 | 8.3385 | 11.6713 | 15.4321 | 20.2419 | 24.7703 | 27.6102 | 17.5053
3423 | 27.381 | 24.0764 | 20.2151 | 14.3051 | 9.6055 | 7.5552 | 8.3167 | 11.839 | 15.5394 | 20.5912 | 24.8007 | 27.7441 | 17.6641
3424 | 27.4881 | 23.9342 | 20.2737 | 14.4167 | 9.8672 | 7.8769 | 8.5315 | 11.7896 | 15.5576 | 20.6268 | 24.9083 | 28.0181 | 17.7741
3427 | 23.7933 | 20.9672 | 16.9809 | 11.6908 | 7.721 | 6.3091 | 7.1239 | 10.6064 | 13.8578 | 17.9318 | 21.4484 | 24.1909 | 15.2185
3428 | 23.6578 | 20.927 | 16.9251 | 11.5154 | 7.5683 | 6.1296 | 7.0564 | 10.4014 | 13.628 | 17.6663 | 21.4836 | 24.0979 | 15.0881
3429 | 24.0492 | 21.2993 | 17.203 | 11.73 | 7.7458 | 6.2055 | 7.0637 | 10.431 | 13.7328 | 17.9185 | 21.5596 | 24.4388 | 15.2814
3430 | 24.5853 | 21.7583 | 17.6867 | 12.0231 | 7.944 | 6.1274 | 6.9268 | 10.5186 | 13.8819 | 18.3354 | 22.1455 | 25.2542 | 15.5989
3431 | 24.5385 | 21.6126 | 17.5777 | 12.0275 | 7.9285 | 6.0628 | 6.9168 | 10.4513 | 13.9216 | 18.3322 | 22.1915 | 25.1786 | 15.5616
3433 | 25.0187 | 22.1161 | 17.9899 | 12.2006 | 7.9622 | 6.0321 | 6.81 | 10.5097 | 14.0247 | 18.3113 | 22.4009 | 25.6349 | 15.7509
3434 | 25.5563 | 22.5342 | 18.3433 | 12.3248 | 8.0217 | 6.0207 | 6.8234 | 10.5658 | 14.1244 | 18.4958 | 22.8164 | 26.0441 | 15.9726
3435 | 25.6329 | 22.6076 | 18.4725 | 12.4878 | 8.1486 | 5.9852 | 6.8229 | 10.5288 | 14.1782 | 18.6483 | 23.0263 | 26.3096 | 16.0707
3437 | 24.0453 | 20.9667 | 17.108 | 11.7277 | 7.752 | 5.8627 | 6.7256 | 10.374 | 14.0331 | 18.0435 | 21.7895 | 24.4916 | 15.2433
3438 | 24.4861 | 21.3963 | 17.3407 | 11.86 | 7.6939 | 5.7175 | 6.6072 | 10.2893 | 14.0405 | 18.1902 | 21.9846 | 24.8116 | 15.3681
3440 | 25.1254 | 22.0537 | 18.1442 | 12.1483 | 7.8795 | 5.7304 | 6.6683 | 10.3158 | 14.1141 | 18.4489 | 22.7049 | 25.6224 | 15.7463
3441 | 25.0541 | 22.0337 | 18.1552 | 12.186 | 7.8421 | 5.7415 | 6.697 | 10.3496 | 14.1683 | 18.5282 | 22.5738 | 25.6247 | 15.7462
3442 | 25.7122 | 22.5577 | 18.5684 | 12.3771 | 8.0349 | 5.8342 | 6.74 | 10.3504 | 14.2687 | 18.6697 | 23.0047 | 26.262 | 16.0317
3444 | 26.6716 | 23.6831 | 19.4816 | 13.0926 | 8.5349 | 6.1339 | 7.0507 | 10.6254 | 14.3749 | 19.3635 | 24.3256 | 27.6159 | 16.7461
3446 | 26.5178 | 23.4421 | 19.2633 | 12.9275 | 8.3042 | 6.0132 | 6.9642 | 10.5853 | 14.2367 | 19.0773 | 23.9603 | 27.1887 | 16.5401
3447 | 26.6604 | 23.6379 | 19.4217 | 13.0539 | 8.4454 | 6.1538 | 7.0281 | 10.6822 | 14.3634 | 19.2477 | 24.1234 | 27.4449 | 16.6886
3448 | 26.854 | 23.9248 | 19.7361 | 13.3142 | 8.6085 | 6.3566 | 7.1807 | 10.9007 | 14.4755 | 19.7225 | 24.4545 | 27.9108 | 16.9532
3450 | 26.6387 | 23.709 | 19.6241 | 13.306 | 8.4759 | 6.3161 | 7.1987 | 10.7872 | 14.6803 | 19.469 | 24.053 | 27.4681 | 16.8105
3451 | 26.5351 | 23.5372 | 19.3845 | 13.2169 | 8.3851 | 6.2717 | 7.1307 | 10.7209 | 14.6103 | 19.2173 | 23.7755 | 27.2919 | 16.6731
3453 | 26.9062 | 23.9431 | 19.7773 | 13.5549 | 8.6948 | 6.4351 | 7.3261 | 10.9033 | 14.8049 | 19.7366 | 24.1929 | 27.8088 | 17.007
3458 | 25.9442 | 22.6532 | 18.5258 | 12.4625 | 7.9952 | 5.8029 | 6.7402 | 10.2938 | 14.0577 | 18.5331 | 23.2943 | 26.4551 | 16.0632
3460 | 25.9742 | 22.784 | 18.6278 | 12.4081 | 7.8268 | 5.7122 | 6.6546 | 10.1661 | 13.9578 | 18.4153 | 23.1181 | 26.5425 | 16.0156
3461 | 26.2426 | 23.113 | 18.8147 | 12.6668 | 7.9745 | 5.87 | 6.8037 | 10.321 | 14.1618 | 18.5744 | 23.3056 | 26.8 | 16.2207
3462 | 26.5919 | 23.6819 | 19.2801 | 13.1346 | 8.4661 | 6.3116 | 7.2201 | 10.733 | 14.5702 | 19.462 | 23.8168 | 27.327 | 16.7163
3463 | 26.9307 | 23.9054 | 19.8597 | 13.5253 | 8.853 | 6.6119 | 7.4761 | 10.9898 | 14.7505 | 19.9772 | 24.3139 | 27.6652 | 17.0716
3464 | 26.8826 | 23.8035 | 19.562 | 13.3683 | 8.8043 | 6.5545 | 7.3932 | 10.9209 | 14.6598 | 19.5979 | 24.3087 | 27.4543 | 16.9425
3465 | 26.9084 | 23.5122 | 19.4932 | 13.2219 | 8.6674 | 6.5652 | 7.4016 | 11.0295 | 15.0749 | 19.864 | 24.1303 | 27.4299 | 16.9415
3467 | 26.6885 | 23.5653 | 19.4469 | 13.2005 | 8.6224 | 6.5045 | 7.4131 | 10.9835 | 14.7803 | 19.7678 | 24.1762 | 27.266 | 16.8679
3468 | 26.5392 | 23.1429 | 18.7331 | 12.8466 | 8.4039 | 6.3586 | 7.1198 | 10.8256 | 14.5861 | 19.2538 | 23.7652 | 27.1735 | 16.5624
3469 | 26.4312 | 22.9824 | 19.0754 | 12.9835 | 8.315 | 6.2304 | 6.9787 | 10.652 | 14.6539 | 19.2528 | 23.7312 | 26.9518 | 16.5199
3472 | 26.7613 | 23.4254 | 19.8701 | 13.6685 | 8.9632 | 6.6774 | 7.5236 | 11.2232 | 15.0954 | 20.0075 | 24.1611 | 27.5645 | 17.0784
3475 | 26.8373 | 23.4559 | 19.777 | 13.6879 | 8.9592 | 6.6534 | 7.5157 | 11.2249 | 15.2477 | 19.923 | 24.1756 | 27.5804 | 17.0865
3477 | 27.3762 | 23.8083 | 20.1009 | 13.734 | 9.0748 | 6.9067 | 7.5825 | 11.2723 | 15.2097 | 20.3328 | 24.7444 | 27.8891 | 17.336
3478 | 27.4563 | 24.0201 | 20.3054 | 14.0084 | 9.4935 | 7.2334 | 7.8348 | 11.2279 | 14.931 | 20.3069 | 24.8421 | 27.7738 | 17.4528
3480 | 27.4424 | 23.9508 | 20.5829 | 14.2719 | 9.6518 | 7.5164 | 8.1846 | 11.7303 | 15.488 | 20.5291 | 24.6642 | 27.8848 | 17.6581
3482 | 27.823 | 24.2086 | 20.6948 | 14.6224 | 10.0544 | 7.7843 | 8.4225 | 11.9197 | 15.6198 | 20.8709 | 24.9552 | 28.0719 | 17.9206
3483 | 27.9007 | 24.2151 | 20.7598 | 14.6783 | 10.0671 | 7.8266 | 8.4107 | 12.0122 | 15.7235 | 20.9369 | 25.0556 | 28.1002 | 17.9739
3485 | 27.9333 | 24.3129 | 20.9349 | 14.9025 | 10.0959 | 7.9928 | 8.6015 | 12.3196 | 16.0113 | 21.4373 | 25.1229 | 28.1387 | 18.1503
3490 | 28.1788 | 24.3902 | 21.5186 | 15.2203 | 10.3625 | 8.1877 | 9.0333 | 12.8034 | 16.6574 | 21.694 | 25.293 | 28.4081 | 18.479
3491 | 27.7293 | 24.1009 | 20.8137 | 14.5992 | 10.0748 | 8.0729 | 8.6827 | 12.4623 | 16.1629 | 21.4243 | 25.1903 | 28.1604 | 18.1228
3494 | 28.3596 | 24.5837 | 21.6452 | 15.3795 | 10.6714 | 8.695 | 9.3336 | 13.1919 | 17.0796 | 22.2827 | 25.1869 | 28.0652 | 18.7062
3496 | 28.4162 | 24.4552 | 21.5481 | 15.5973 | 10.7078 | 8.7081 | 9.6166 | 13.1646 | 17.0427 | 22.2922 | 25.5857 | 28.3704 | 18.7921
3498 | 28.4816 | 24.584 | 21.7719 | 15.6833 | 10.6966 | 8.7395 | 9.4754 | 13.3529 | 17.3262 | 22.2665 | 25.5161 | 28.6036 | 18.8748
3500 | 28.5858 | 24.6196 | 21.8123 | 15.675 | 10.7946 | 8.7924 | 9.5479 | 13.3865 | 17.186 | 22.3291 | 25.5428 | 28.6789 | 18.9126
3501 | 28.1424 | 24.4599 | 21.5305 | 15.3469 | 10.4521 | 8.4659 | 9.194 | 13.0203 | 16.9669 | 22.0636 | 25.3055 | 28.5834 | 18.6276
3505 | 28.6251 | 24.5973 | 21.6494 | 15.7301 | 10.7986 | 8.7805 | 9.5593 | 13.3298 | 17.2068 | 22.2538 | 25.7277 | 28.7782 | 18.9197
3507 | 28.0839 | 24.217 | 21.0483 | 14.9054 | 10.2828 | 8.3382 | 8.9349 | 12.742 | 16.6932 | 21.7753 | 25.4716 | 28.5376 | 18.4192
3509 | 28.0301 | 24.3081 | 20.7005 | 14.8536 | 10.3623 | 8.2332 | 8.9371 | 12.5198 | 16.2517 | 21.5504 | 25.3632 | 28.2036 | 18.2761
3512 | 27.8412 | 24.4416 | 20.7969 | 14.7799 | 10.3476 | 8.1309 | 9.0166 | 12.5124 | 16.2341 | 21.3497 | 25.3901 | 28.0156 | 18.2381
3515 | 26.9603 | 24.0951 | 20.2931 | 13.7884 | 9.1183 | 6.866 | 7.6357 | 11.291 | 15.1918 | 20.3974 | 24.4572 | 27.7504 | 17.3204
3516 | 27.1431 | 24.2875 | 20.4244 | 13.9551 | 9.546 | 7.1478 | 7.8911 | 11.5669 | 15.2444 | 20.8019 | 24.8334 | 28.0725 | 17.5762
3517 | 27.2684 | 24.1878 | 20.4991 | 14.1142 | 9.628 | 7.2585 | 8.0319 | 11.7274 | 15.3641 | 20.9228 | 25.0137 | 28.0544 | 17.6725
3518 | 27.5466 | 24.0346 | 20.3066 | 14.0164 | 9.4045 | 7.08 | 7.8486 | 11.5501 | 15.4395 | 20.5011 | 24.8131 | 28.1325 | 17.5561
3520 | 27.4298 | 24.1447 | 20.6476 | 14.3741 | 9.7312 | 7.4739 | 8.1172 | 11.8032 | 15.5316 | 20.9052 | 24.9883 | 28.2864 | 17.7861
3521 | 26.6115 | 23.5687 | 19.4215 | 12.986 | 8.4974 | 6.0934 | 6.9409 | 10.6902 | 14.435 | 19.1649 | 24.0072 | 27.5796 | 16.6664
3522 | 26.5645 | 23.7015 | 19.8014 | 13.2306 | 8.7174 | 6.2918 | 7.1141 | 10.8298 | 14.646 | 19.3835 | 24.1527 | 27.566 | 16.8333
3523 | 26.7598 | 23.9271 | 20.245 | 13.576 | 9.0137 | 6.5984 | 7.5218 | 11.2224 | 15.0601 | 20.1063 | 24.5059 | 27.7713 | 17.1923
3525 | 27.4883 | 24.3081 | 20.5642 | 14.3877 | 9.7949 | 7.4465 | 8.078 | 11.6728 | 15.4291 | 20.6819 | 24.9027 | 28.0146 | 17.7307
3527 | 27.7013 | 24.2914 | 20.7063 | 14.5237 | 10.0771 | 7.7142 | 8.3903 | 11.9665 | 15.7301 | 20.8959 | 24.9601 | 28.1963 | 17.9294
3530 | 27.6721 | 24.2254 | 20.9895 | 14.8548 | 10.1686 | 7.97 | 8.5805 | 12.2462 | 15.8992 | 21.3276 | 25.272 | 28.3178 | 18.127
3531 | 27.8802 | 24.3032 | 20.9649 | 14.901 | 10.2119 | 7.9825 | 8.5345 | 12.2185 | 15.8968 | 21.3573 | 25.1721 | 28.2893 | 18.1427
3533 | 26.8604 | 23.9903 | 21.0771 | 14.8139 | 10.3556 | 8.2945 | 8.8805 | 12.5438 | 16.2138 | 20.5456 | 23.8612 | 26.6059 | 17.8369
3537 | 27.7271 | 24.2752 | 20.8687 | 14.7136 | 10.0559 | 7.6546 | 8.2747 | 11.9395 | 15.6238 | 21.0286 | 24.9729 | 28.3117 | 17.9539
3540 | 27.8692 | 24.3153 | 21.0726 | 14.8186 | 10.1404 | 7.8463 | 8.4855 | 12.1525 | 15.8533 | 21.1765 | 25.0833 | 28.2531 | 18.0889
3542 | 28.0939 | 24.4798 | 21.4316 | 15.0674 | 10.2324 | 8.054 | 8.6303 | 12.2252 | 15.9598 | 21.5139 | 25.2073 | 28.2064 | 18.2585
3544 | 28.0431 | 24.4691 | 21.3312 | 15.1066 | 10.3502 | 8.2027 | 8.8295 | 12.5536 | 16.3362 | 21.7652 | 25.3679 | 28.2359 | 18.3826
3546 | 28.1253 | 24.3008 | 21.283 | 15.2838 | 10.5087 | 8.4454 | 9.1321 | 12.8083 | 16.6045 | 22.1044 | 25.4318 | 28.3296 | 18.5298
3549 | 28.3084 | 24.402 | 21.2833 | 15.4179 | 10.5851 | 8.5167 | 9.2973 | 13.1155 | 16.7146 | 22.2038 | 25.4317 | 28.4757 | 18.646
3550 | 27.0219 | 23.9035 | 20.1571 | 13.777 | 9.0776 | 6.7633 | 7.6259 | 11.3336 | 15.1487 | 20.2584 | 24.4753 | 27.8539 | 17.283
3551 | 26.8573 | 23.7537 | 20.1341 | 13.7346 | 9.1179 | 6.6639 | 7.6214 | 11.3325 | 14.9429 | 20.0978 | 24.6818 | 27.9726 | 17.2425
3555 | 26.94 | 23.9344 | 20.1335 | 13.7173 | 9.0207 | 6.7178 | 7.5448 | 11.2182 | 14.9601 | 20.1884 | 24.3535 | 27.8433 | 17.2143
3556 | 26.9879 | 23.9875 | 20.3 | 14.0102 | 9.2314 | 6.9343 | 7.8084 | 11.5386 | 15.3532 | 20.5984 | 24.5018 | 27.8793 | 17.4276
3557 | 27.2647 | 24.3858 | 20.4472 | 14.0327 | 9.4919 | 7.0045 | 7.9182 | 11.3859 | 15.0339 | 20.5823 | 24.9991 | 28.2422 | 17.5657
3558 | 27.2872 | 24.4488 | 20.5188 | 14.197 | 9.7479 | 7.2135 | 8.0314 | 11.6202 | 15.3508 | 20.9096 | 25.0696 | 28.2557 | 17.7209
3559 | 27.3257 | 24.3977 | 20.8978 | 14.3947 | 9.7058 | 7.0928 | 7.9294 | 11.5536 | 15.4593 | 20.692 | 25.0171 | 28.1917 | 17.7215
3561 | 27.7645 | 24.4774 | 21.0763 | 14.4892 | 9.8091 | 7.3448 | 8.1728 | 11.7848 | 15.4377 | 21.0621 | 25.1142 | 28.757 | 17.9408
3562 | 27.6137 | 23.9905 | 20.7909 | 14.6308 | 9.8852 | 7.5752 | 8.2947 | 12.1415 | 15.7727 | 21.1767 | 25.0428 | 28.4922 | 17.9506
3563 | 27.7284 | 24.3863 | 20.9389 | 14.452 | 9.8134 | 7.4117 | 8.1719 | 11.9368 | 15.5274 | 20.9812 | 25.0055 | 28.7917 | 17.9288
3564 | 27.5955 | 24.1081 | 21.0313 | 14.4939 | 9.8599 | 7.4455 | 8.2636 | 11.914 | 15.7304 | 20.9724 | 24.8596 | 28.5072 | 17.8985
3566 | 27.5932 | 24.0203 | 20.9131 | 14.7571 | 9.7954 | 7.485 | 8.3291 | 12.1467 | 15.8632 | 20.9857 | 25.0602 | 28.3744 | 17.9436
3567 | 27.5828 | 23.9524 | 20.8447 | 14.7007 | 9.8173 | 7.5033 | 8.3426 | 12.1472 | 15.8077 | 21.0121 | 24.8897 | 28.329 | 17.9108
3568 | 27.4311 | 23.7891 | 20.8304 | 14.7038 | 9.853 | 7.5535 | 8.3376 | 12.2297 | 16.0566 | 20.9126 | 24.8437 | 28.2688 | 17.9008
3570 | 27.1212 | 24.2593 | 20.3806 | 14.0169 | 9.4862 | 7.1189 | 7.9602 | 11.6322 | 15.4077 | 20.7605 | 24.9619 | 27.9443 | 17.5875
3571 | 27.5163 | 24.2767 | 20.613 | 14.3743 | 9.8608 | 7.3803 | 8.1686 | 11.8454 | 15.5625 | 21.0286 | 25.1388 | 28.2826 | 17.8373
3572 | 27.5403 | 24.4682 | 20.7828 | 14.3397 | 9.7539 | 7.2782 | 8.1224 | 11.7943 | 15.3802 | 20.9081 | 25.0965 | 28.6164 | 17.8401
3573 | 27.3589 | 24.156 | 20.7193 | 14.5258 | 10.0163 | 7.5072 | 8.2911 | 12.0466 | 15.7137 | 21.1779 | 24.9198 | 28.3616 | 17.8995
3575 | 27.6838 | 24.2394 | 20.8656 | 14.7167 | 9.9781 | 7.5203 | 8.3205 | 12.1871 | 15.7967 | 21.1273 | 25.3167 | 28.5438 | 18.0247
3579 | 28.044 | 24.3911 | 21.1781 | 14.9464 | 10.0908 | 7.76 | 8.5105 | 12.3176 | 15.9297 | 21.3942 | 25.4275 | 28.7885 | 18.2315
3580 | 27.7812 | 24.0355 | 21.1219 | 14.8829 | 9.952 | 7.7336 | 8.5102 | 12.4422 | 16.2554 | 21.3707 | 25.1624 | 28.4419 | 18.1408
3581 | 28.0711 | 24.2614 | 21.2631 | 15.049 | 10.114 | 7.8728 | 8.5827 | 12.3746 | 15.9614 | 21.3061 | 25.2761 | 28.4281 | 18.2134
3584 | 28.1044 | 24.2644 | 21.474 | 15.0464 | 10.1821 | 8.0111 | 8.7089 | 12.5728 | 16.2815 | 21.7915 | 25.6457 | 28.506 | 18.3824
3585 | 28.1174 | 24.4853 | 21.4231 | 15.2592 | 10.3014 | 8.1526 | 8.755 | 12.3999 | 16.1928 | 21.7135 | 25.3314 | 28.2849 | 18.368
3586 | 28.0845 | 24.4408 | 21.6188 | 15.084 | 10.1791 | 8.0741 | 8.7609 | 12.5309 | 16.3378 | 21.9173 | 25.6029 | 28.4711 | 18.4252
3588 | 28.1947 | 24.5036 | 21.411 | 15.2109 | 10.3425 | 8.206 | 8.8721 | 12.6045 | 16.4314 | 21.9106 | 25.4846 | 28.5539 | 18.4772
3589 | 28.1947 | 24.5036 | 21.411 | 15.2109 | 10.3425 | 8.206 | 8.8721 | 12.6045 | 16.4314 | 21.9106 | 25.4846 | 28.5539 | 18.4772
3590 | 28.2795 | 24.4817 | 21.497 | 15.1833 | 10.3024 | 8.2441 | 8.8978 | 12.6334 | 16.4923 | 22.062 | 25.6783 | 28.5706 | 18.5269
3591 | 28.1763 | 24.3987 | 21.2949 | 15.1892 | 10.3893 | 8.2441 | 8.8683 | 12.595 | 16.5679 | 21.9348 | 25.5058 | 28.5907 | 18.4796
3594 | 28.2542 | 24.3819 | 21.4432 | 15.1993 | 10.3863 | 8.3166 | 8.9081 | 12.7382 | 16.5457 | 21.9981 | 25.6317 | 28.5088 | 18.526
3595 | 28.1768 | 24.3729 | 21.3536 | 15.2139 | 10.3517 | 8.2816 | 8.8839 | 12.5925 | 16.5702 | 21.927 | 25.6161 | 28.4984 | 18.4866
3596 | 28.2442 | 24.2697 | 21.3626 | 15.2045 | 10.3718 | 8.3385 | 8.9222 | 12.6485 | 16.5164 | 22.0158 | 25.6724 | 28.5355 | 18.5085
3597 | 28.1408 | 24.4667 | 21.4224 | 15.3085 | 10.4931 | 8.4526 | 9.1232 | 12.8974 | 16.7462 | 22.2489 | 25.508 | 28.1015 | 18.5758
3608 | 27.0542 | 23.9809 | 20.3596 | 13.8761 | 9.1275 | 6.6506 | 7.4669 | 11.2221 | 14.9294 | 20.0432 | 24.5252 | 27.8355 | 17.2559
3610 | 27.3723 | 24.3448 | 20.8278 | 14.0359 | 9.3785 | 6.9071 | 7.7501 | 11.4017 | 15.161 | 20.4939 | 25.006 | 28.3678 | 17.5873
3612 | 26.8292 | 23.8666 | 20.7087 | 13.9765 | 9.2665 | 6.7578 | 7.665 | 11.488 | 15.3628 | 20.315 | 24.4493 | 27.6394 | 17.3604
3614 | 27.5331 | 24.2934 | 20.9132 | 14.2399 | 9.5043 | 6.9706 | 7.8345 | 11.4526 | 15.2015 | 20.4041 | 24.9516 | 28.5605 | 17.6549
3616 | 27.952 | 24.4355 | 21.0617 | 14.2897 | 9.6294 | 7.0598 | 7.9498 | 11.707 | 15.5445 | 20.6397 | 25.1347 | 28.8203 | 17.852
3617 | 27.8991 | 24.5365 | 21.0193 | 14.2829 | 9.6417 | 7.1405 | 8.018 | 11.6435 | 15.4979 | 20.6293 | 25.156 | 28.7128 | 17.8481
3618 | 27.9261 | 24.4581 | 21.1175 | 14.3625 | 9.6745 | 7.1758 | 8.0302 | 11.6528 | 15.5665 | 20.797 | 25.1828 | 28.9039 | 17.904
3620 | 27.8688 | 24.373 | 20.9817 | 14.388 | 9.7383 | 7.2581 | 8.1926 | 11.7401 | 15.535 | 20.8279 | 25.031 | 28.7657 | 17.8917
3621 | 27.92 | 24.3944 | 20.9697 | 14.4276 | 9.7293 | 7.3225 | 8.1536 | 11.7172 | 15.5026 | 20.9226 | 25.1185 | 28.7506 | 17.9107
3622 | 27.8764 | 24.3317 | 20.9484 | 14.4344 | 9.7963 | 7.3351 | 8.1715 | 11.7224 | 15.5059 | 20.8938 | 25.1432 | 28.6575 | 17.9014
3623 | 27.7611 | 24.5113 | 20.9747 | 14.1909 | 9.5956 | 7.048 | 7.9503 | 11.6916 | 15.418 | 20.6855 | 25.1452 | 28.676 | 17.804
3624 | 27.8301 | 24.4456 | 20.9647 | 14.2644 | 9.647 | 7.1127 | 8.0101 | 11.7085 | 15.4863 | 20.7957 | 25.2531 | 28.7842 | 17.8585
3629 | 27.8491 | 24.2948 | 21.0133 | 14.3818 | 9.7117 | 7.2429 | 8.0907 | 11.7015 | 15.6506 | 20.6817 | 25.0471 | 28.7106 | 17.8647
3630 | 27.679 | 24.1638 | 20.9324 | 14.2105 | 9.6057 | 7.06 | 7.9668 | 11.5968 | 15.3188 | 20.6059 | 25.098 | 28.6908 | 17.744
3631 | 27.3991 | 24.2863 | 20.8969 | 14.2326 | 9.5258 | 6.9936 | 7.8756 | 11.3602 | 15.1014 | 20.5522 | 24.8526 | 28.5628 | 17.6366
3633 | 27.8028 | 24.365 | 20.9435 | 14.3816 | 9.7083 | 7.1483 | 8.0989 | 11.6846 | 15.3769 | 20.7875 | 25.2152 | 28.9115 | 17.8687
3634 | 27.9167 | 24.3455 | 21.0319 | 14.4428 | 9.8023 | 7.1998 | 8.1786 | 11.6423 | 15.4028 | 20.8506 | 25.3105 | 28.9199 | 17.9203
3635 | 27.9992 | 24.3876 | 21.002 | 14.5013 | 9.8627 | 7.3103 | 8.2451 | 11.8685 | 15.7517 | 20.982 | 25.361 | 28.7328 | 18.0004
3636 | 28.1294 | 24.3316 | 21.2073 | 14.5016 | 9.8878 | 7.3255 | 8.2823 | 11.814 | 15.6411 | 21.1138 | 25.4706 | 29.0864 | 18.066
3637 | 27.8416 | 23.982 | 20.8856 | 14.6829 | 9.9624 | 7.545 | 8.433 | 11.9075 | 15.8186 | 21.1319 | 25.0572 | 28.5626 | 17.9842
3638 | 28.0094 | 24.4671 | 21.068 | 14.5485 | 9.859 | 7.3832 | 8.2748 | 11.9272 | 15.7989 | 21.0489 | 25.2712 | 28.6899 | 18.0288
3639 | 27.3122 | 23.6691 | 20.8393 | 14.563 | 9.854 | 7.4555 | 8.3221 | 12.0077 | 15.7151 | 20.9928 | 24.9235 | 28.1783 | 17.8194
3640 | 28.2203 | 24.3549 | 21.2268 | 14.6221 | 9.9072 | 7.4563 | 8.3847 | 11.9811 | 15.8457 | 21.2208 | 25.4968 | 29.2498 | 18.1639
3641 | 27.8223 | 24.0931 | 21.1243 | 14.5909 | 9.953 | 7.5537 | 8.4744 | 11.9842 | 15.9655 | 21.2415 | 25.2009 | 28.5588 | 18.0469
3644 | 27.982 | 24.3936 | 21.3332 | 14.7601 | 10.1088 | 7.6102 | 8.5016 | 11.9566 | 15.8964 | 21.3262 | 25.3508 | 28.6919 | 18.1593
3646 | 27.4926 | 24.2061 | 20.9607 | 14.4446 | 9.7369 | 7.1916 | 8.1179 | 11.4966 | 15.1575 | 20.5644 | 24.9152 | 28.5577 | 17.7368
3649 | 27.9789 | 24.2352 | 21.14 | 14.5987 | 9.8621 | 7.4235 | 8.3573 | 11.8445 | 15.6293 | 20.9733 | 25.2366 | 28.9893 | 18.0224
3658 | 25.9127 | 22.9514 | 18.6609 | 12.5096 | 7.9991 | 5.7385 | 6.5449 | 10.285 | 13.7448 | 18.472 | 22.9748 | 26.0995 | 15.9911
3659 | 26.2001 | 23.3666 | 19.3363 | 12.8367 | 8.2198 | 5.9946 | 6.8029 | 10.6259 | 14.1347 | 19.1197 | 23.5777 | 26.6675 | 16.4069
3660 | 26.4618 | 23.7061 | 19.5599 | 13.1419 | 8.582 | 6.1305 | 7.017 | 10.6519 | 14.3612 | 19.3675 | 23.7639 | 27.145 | 16.6574
3662 | 26.6762 | 23.8522 | 20.0796 | 13.5066 | 8.8477 | 6.3939 | 7.3172 | 10.9629 | 14.7811 | 19.643 | 24.3028 | 27.5749 | 16.9948
3663 | 26.8482 | 24.0413 | 20.1291 | 13.6145 | 9.0032 | 6.4794 | 7.2998 | 11.0083 | 14.6937 | 19.9019 | 24.4268 | 27.7615 | 17.1006
3664 | 26.8271 | 23.9137 | 20.0868 | 13.5511 | 8.8545 | 6.3614 | 7.1901 | 10.9317 | 14.5317 | 19.7831 | 24.2466 | 27.6204 | 16.9915
3666 | 26.865 | 23.9724 | 20.1974 | 13.5945 | 8.9259 | 6.4334 | 7.3094 | 11.0103 | 14.5261 | 19.7973 | 24.2019 | 27.9776 | 17.0676
3669 | 26.833 | 24.047 | 20.576 | 13.9515 | 9.2328 | 6.7009 | 7.6299 | 11.199 | 14.9287 | 20.3129 | 24.5984 | 28.2573 | 17.3556
3670 | 26.9222 | 23.928 | 20.2205 | 13.8204 | 9.0785 | 6.4705 | 7.4213 | 10.9341 | 14.6781 | 20.0122 | 24.5125 | 28.0939 | 17.1744
3672 | 27.1248 | 24.0946 | 20.7886 | 14.0655 | 9.3324 | 6.7906 | 7.7258 | 11.1485 | 14.9781 | 20.1529 | 24.7599 | 28.08 | 17.4201
3673 | 26.983 | 23.6916 | 20.2949 | 13.6948 | 8.8888 | 6.42 | 7.4513 | 10.8433 | 14.5548 | 19.9996 | 24.3489 | 28.1471 | 17.1098
3675 | 27.2748 | 23.9274 | 20.4104 | 13.6742 | 9.1646 | 6.6105 | 7.6038 | 10.981 | 14.7725 | 20.1491 | 24.7032 | 28.3925 | 17.3053
3677 | 27.5274 | 24.1194 | 20.7006 | 14.1033 | 9.4615 | 6.9136 | 7.8845 | 11.3788 | 15.1595 | 20.3774 | 24.7934 | 28.4394 | 17.5716
3678 | 27.3942 | 24.1878 | 20.5929 | 13.9655 | 9.332 | 6.7128 | 7.7977 | 11.213 | 15.0695 | 20.3086 | 24.5299 | 28.3436 | 17.454
3682 | 27.6259 | 24.1609 | 20.8649 | 14.246 | 9.6114 | 7.0473 | 8.0891 | 11.4878 | 15.2011 | 20.5593 | 24.8783 | 28.6485 | 17.7017
3683 | 27.1329 | 23.9346 | 20.7779 | 14.1205 | 9.3819 | 6.8661 | 7.9665 | 11.4301 | 15.1643 | 20.7104 | 24.6605 | 28.0933 | 17.5199
3685 | 27.5672 | 24.1296 | 20.8599 | 14.3137 | 9.6682 | 7.1565 | 8.1354 | 11.602 | 15.4402 | 20.7186 | 24.9114 | 28.513 | 17.7513
3687 | 27.4994 | 24.334 | 20.9698 | 14.3817 | 9.776 | 7.2823 | 8.1986 | 11.693 | 15.5506 | 20.8453 | 24.9829 | 28.4407 | 17.8295
3688 | 27.4953 | 24.1203 | 20.7397 | 14.2556 | 9.5091 | 6.9504 | 7.9953 | 11.4078 | 15.226 | 20.6095 | 24.8265 | 28.3585 | 17.6245
3690 | 27.3251 | 23.9409 | 20.7654 | 14.1491 | 9.4527 | 6.9078 | 7.8626 | 11.3855 | 15.2653 | 20.635 | 24.7809 | 28.2771 | 17.5623
3691 | 26.9009 | 23.6509 | 20.107 | 13.6643 | 8.9598 | 6.3988 | 7.4219 | 10.8302 | 14.3387 | 19.7885 | 24.2609 | 27.9619 | 17.0237
3694 | 27.5208 | 24.113 | 20.7554 | 14.0408 | 9.3319 | 6.8734 | 7.8536 | 11.3812 | 15.1807 | 20.4771 | 24.6607 | 28.3444 | 17.5444
3695 | 27.1357 | 23.919 | 20.2527 | 13.7117 | 9.0346 | 6.5204 | 7.5954 | 10.9194 | 14.6259 | 19.955 | 24.4226 | 28.1186 | 17.1842
3697 | 25.7386 | 22.7139 | 19.0747 | 13.1338 | 8.4601 | 6.1028 | 6.8901 | 9.9112 | 13.3796 | 18.6433 | 23.0635 | 27.1259 | 16.1865
3698 | 26.1453 | 22.9636 | 19.2414 | 13.0083 | 8.4355 | 6.0955 | 6.9467 | 9.9994 | 13.5051 | 18.8697 | 23.3382 | 27.4067 | 16.3296
3699 | 25.7619 | 22.8204 | 18.9547 | 13.0192 | 8.3539 | 6.0932 | 6.8557 | 9.7483 | 13.2286 | 18.5326 | 22.9879 | 27.1452 | 16.1251
3700 | 26.9549 | 23.7378 | 20.2911 | 13.9746 | 9.1092 | 6.5976 | 7.6094 | 11.0539 | 14.8149 | 20.0389 | 24.1445 | 28.1192 | 17.2038
3701 | 26.4765 | 23.3823 | 20.022 | 13.4955 | 8.6592 | 6.2153 | 7.2968 | 10.4753 | 14.1303 | 19.444 | 23.7939 | 27.7256 | 16.7597
3705 | 26.4706 | 23.3905 | 19.9695 | 13.7305 | 8.8582 | 6.4803 | 7.5328 | 10.7603 | 14.3957 | 19.4526 | 23.6777 | 27.6346 | 16.8628
3707 | 25.9323 | 22.9748 | 19.8363 | 13.411 | 8.6643 | 6.2199 | 7.3072 | 10.739 | 14.4739 | 19.2838 | 23.7596 | 27.1671 | 16.6474
3709 | 27.0556 | 23.8651 | 20.219 | 13.9173 | 9.0594 | 6.583 | 7.5577 | 11.0469 | 14.6905 | 19.9067 | 24.1809 | 28.0975 | 17.1816
3711 | 25.776 | 22.7913 | 18.4876 | 12.4488 | 7.8265 | 5.4227 | 6.2406 | 9.759 | 13.1188 | 18.0095 | 22.8663 | 26.3302 | 15.7564
3712 | 26.0528 | 23.1795 | 19.1911 | 12.8102 | 8.0615 | 5.7695 | 6.7339 | 9.9544 | 13.85 | 18.6463 | 23.0906 | 26.8933 | 16.1861
3713 | 25.4909 | 22.4605 | 18.297 | 12.34 | 7.617 | 5.3285 | 6.1521 | 9.618 | 13.1655 | 18.0527 | 22.508 | 25.9855 | 15.5846
3714 | 26.2536 | 23.4841 | 19.2164 | 12.8549 | 8.0137 | 5.7493 | 6.7122 | 10.194 | 13.8936 | 18.6306 | 23.5345 | 27.1166 | 16.3044
3715 | 26.7451 | 23.7235 | 19.7824 | 13.1865 | 8.4717 | 6.0609 | 6.9673 | 10.4331 | 14.2995 | 19.2026 | 23.7643 | 27.6624 | 16.6916
3717 | 25.9583 | 23.1589 | 18.7578 | 12.5167 | 7.8958 | 5.5202 | 6.5047 | 10.2863 | 13.7753 | 18.4791 | 23.3272 | 26.4315 | 16.051
3719 | 26.5926 | 23.7132 | 19.5428 | 13.1827 | 8.3857 | 6.0471 | 7.0059 | 10.384 | 14.0276 | 19.0787 | 23.8263 | 27.3261 | 16.5927
3720 | 26.2852 | 23.3799 | 19.5409 | 13.3234 | 8.4119 | 5.8991 | 6.7812 | 10.2944 | 14.0899 | 19.077 | 23.5732 | 27.0661 | 16.4769
3722 | 26.4243 | 23.6154 | 19.6935 | 13.2162 | 8.6317 | 6.1851 | 7.0522 | 10.4163 | 14.0912 | 19.1652 | 23.7974 | 27.3606 | 16.6374
3723 | 25.4208 | 22.6448 | 19.0381 | 12.65 | 7.9795 | 5.7162 | 6.5177 | 9.7853 | 13.3454 | 18.4386 | 22.83 | 26.6185 | 15.9154
3725 | 27.3077 | 24.1137 | 20.8452 | 14.2164 | 9.6097 | 7.0229 | 7.8509 | 11.2331 | 14.9737 | 20.467 | 24.8828 | 28.169 | 17.5577
3726 | 27.1758 | 24.0716 | 20.8302 | 14.1176 | 9.466 | 6.9836 | 7.8074 | 11.1323 | 15.033 | 20.4184 | 24.6005 | 28.0393 | 17.473
3727 | 27.5144 | 24.2351 | 21.0032 | 14.5803 | 9.8813 | 7.3183 | 8.113 | 11.4405 | 15.2089 | 20.7509 | 25.0195 | 28.4283 | 17.7911
3728 | 27.5839 | 24.1181 | 21.015 | 14.4382 | 9.7444 | 7.2773 | 8.1527 | 11.5279 | 15.3577 | 20.8047 | 25.0855 | 28.58 | 17.8071
3730 | 27.7094 | 23.9159 | 20.969 | 14.6369 | 9.8911 | 7.3893 | 8.3059 | 11.7077 | 15.634 | 20.9759 | 25.1369 | 28.793 | 17.9221
3732 | 27.1632 | 23.9219 | 20.3862 | 13.6901 | 9.1419 | 6.5388 | 7.6051 | 11.041 | 14.8281 | 20.2359 | 24.7077 | 28.3093 | 17.2974
3733 | 26.6923 | 23.5112 | 20.086 | 13.4468 | 8.7473 | 6.1964 | 7.2063 | 10.6062 | 14.2675 | 19.7546 | 24.2895 | 27.9581 | 16.8969
3735 | 27.0119 | 23.8267 | 20.1617 | 13.6413 | 8.9547 | 6.5175 | 7.4434 | 10.7393 | 14.5013 | 19.9665 | 24.1724 | 28.2 | 17.0947
3737 | 25.7528 | 22.6844 | 19.3894 | 13.0327 | 8.3651 | 5.9137 | 6.695 | 9.7389 | 13.7426 | 18.7349 | 23.0417 | 27.2564 | 16.1956
3739 | 26.6588 | 23.4293 | 20.0181 | 13.4518 | 8.6382 | 6.1977 | 7.2126 | 10.5236 | 14.1627 | 19.5086 | 23.8998 | 28.0929 | 16.8162
3740 | 26.0989 | 22.9558 | 19.5374 | 13.1485 | 8.5645 | 6.0595 | 7.0444 | 10.1775 | 13.8483 | 19.2316 | 23.4475 | 27.6327 | 16.4789
3741 | 24.3477 | 21.6817 | 18.2255 | 12.5527 | 7.9594 | 5.4179 | 6.0514 | 9.4933 | 13.8068 | 18.4355 | 22.304 | 26.0861 | 15.5302
3744 | 26.0021 | 22.9385 | 19.3871 | 13.2248 | 8.5828 | 6.014 | 6.9363 | 10.1213 | 13.6406 | 19.0711 | 23.3576 | 27.5882 | 16.4054
3746 | 27.0016 | 23.6196 | 20.5392 | 13.9886 | 9.1716 | 6.7264 | 7.8148 | 11.2487 | 15.127 | 20.1753 | 24.068 | 28.006 | 17.2906
3747 | 26.958 | 23.3642 | 20.1942 | 13.6273 | 8.9096 | 6.493 | 7.4818 | 10.8315 | 14.3789 | 19.7431 | 24.0011 | 28.0546 | 17.0031
3749 | 27.1247 | 23.5425 | 20.2176 | 13.6866 | 9.0778 | 6.5104 | 7.4446 | 10.8228 | 14.5028 | 19.8326 | 24.3546 | 28.1128 | 17.1025
3750 | 23.9404 | 21.3546 | 17.1576 | 11.5204 | 7.4633 | 6.0208 | 6.8216 | 10.1305 | 13.344 | 17.4898 | 21.467 | 24.3702 | 15.09
3751 | 24.0903 | 21.3924 | 17.0882 | 11.439 | 7.4806 | 5.9498 | 6.7105 | 10.1401 | 13.3183 | 17.3502 | 21.4723 | 24.2321 | 15.0553
3752 | 23.8202 | 21.1949 | 16.9549 | 11.3506 | 7.3824 | 5.9428 | 6.6986 | 10.0478 | 13.2279 | 17.27 | 21.5257 | 24.1092 | 14.9604
3753 | 24.3367 | 21.6048 | 17.4618 | 11.7499 | 7.6089 | 5.8933 | 6.7213 | 10.2884 | 13.5118 | 17.6357 | 21.5586 | 24.6076 | 15.2482
3754 | 23.8558 | 21.2622 | 17.0057 | 11.3856 | 7.3975 | 5.9085 | 6.6796 | 10.0678 | 13.2299 | 17.2931 | 21.3815 | 24.0418 | 14.9591
3755 | 23.6248 | 21.0532 | 16.8055 | 11.3032 | 7.2775 | 5.7035 | 6.4132 | 9.857 | 12.9977 | 16.8617 | 20.8788 | 23.6662 | 14.7035
3756 | 24.5453 | 21.8525 | 17.7632 | 11.9769 | 7.7115 | 5.9079 | 6.6395 | 10.3587 | 13.6538 | 17.8276 | 21.9215 | 24.8835 | 15.4202
3757 | 24.6968 | 21.5271 | 17.4082 | 11.8372 | 7.4428 | 5.4608 | 6.3035 | 9.9835 | 13.2455 | 17.6083 | 22.1262 | 24.5158 | 15.1797
3758 | 25.4949 | 22.4699 | 18.4429 | 12.258 | 7.891 | 5.8132 | 6.6848 | 10.3377 | 13.9642 | 18.4356 | 22.5561 | 25.6507 | 15.8332
3759 | 23.6042 | 20.8824 | 16.7429 | 11.2166 | 7.1907 | 5.7771 | 6.5268 | 9.7447 | 12.9083 | 16.6922 | 21.0776 | 23.5762 | 14.6616
3760 | 23.4773 | 20.7552 | 16.6901 | 11.2454 | 7.2033 | 5.7279 | 6.4172 | 9.7061 | 12.7768 | 16.5916 | 20.9886 | 23.4603 | 14.5867
3761 | 23.561 | 20.7478 | 16.7014 | 11.2858 | 7.213 | 5.5184 | 6.2858 | 9.6117 | 12.7892 | 16.6316 | 21.0223 | 23.4278 | 14.5663
3763 | 24.0156 | 21.1827 | 16.8681 | 11.4363 | 7.2698 | 5.3321 | 6.1879 | 9.8172 | 12.8481 | 17.0749 | 21.3116 | 23.7929 | 14.7614
3764 | 26.0525 | 23.1739 | 18.9799 | 12.6392 | 8.3381 | 5.9812 | 6.7422 | 10.6052 | 14.2633 | 18.9583 | 23.4378 | 26.6368 | 16.3174
3765 | 23.7493 | 20.9963 | 16.5177 | 11.0025 | 7.1497 | 5.772 | 6.446 | 9.6561 | 12.6017 | 16.4811 | 20.9073 | 23.5546 | 14.5695
3766 | 23.7493 | 20.9963 | 16.5177 | 11.0025 | 7.1497 | 5.772 | 6.446 | 9.6561 | 12.6017 | 16.4811 | 20.9073 | 23.5546 | 14.5695
3767 | 23.5826 | 20.7204 | 16.2699 | 10.9354 | 7.0345 | 5.6342 | 6.3815 | 9.5911 | 12.6003 | 16.4494 | 20.856 | 23.3354 | 14.4492
3770 | 23.737 | 21.0608 | 16.5728 | 11.2284 | 7.2159 | 5.7343 | 6.4282 | 9.6448 | 12.4278 | 16.644 | 21.1015 | 23.7532 | 14.629
3775 | 23.7358 | 20.8714 | 16.5935 | 11.2601 | 7.249 | 5.4248 | 6.1043 | 9.6637 | 12.6565 | 16.7735 | 21.0415 | 23.4327 | 14.5672
3777 | 23.6357 | 20.7784 | 16.41 | 11.1779 | 6.9897 | 5.1376 | 5.9728 | 9.2978 | 12.3328 | 16.4613 | 20.8381 | 23.0615 | 14.3411
3778 | 25.025 | 22.2181 | 17.534 | 11.8022 | 7.5087 | 5.2174 | 6.0436 | 9.273 | 12.5972 | 17.2253 | 21.7086 | 25.4021 | 15.1296
3779 | 25.025 | 22.2181 | 17.534 | 11.8022 | 7.5087 | 5.2174 | 6.0436 | 9.273 | 12.5972 | 17.2253 | 21.7086 | 25.4021 | 15.1296
3781 | 23.7161 | 20.5917 | 16.174 | 10.8641 | 7.1439 | 5.7219 | 6.4736 | 9.6396 | 12.7027 | 16.3886 | 20.7819 | 23.011 | 14.4341
3782 | 23.6784 | 20.632 | 16.1668 | 10.8722 | 7.1436 | 5.7901 | 6.4648 | 9.6086 | 12.6406 | 16.4449 | 20.8891 | 23.2309 | 14.4635
3783 | 22.9559 | 20.2252 | 16.0426 | 10.6855 | 6.9688 | 5.5248 | 6.1124 | 9.3812 | 12.3617 | 16.0759 | 20.2332 | 22.539 | 14.0922
3785 | 23.5128 | 20.6973 | 16.2243 | 10.9325 | 7.1125 | 5.6466 | 6.4963 | 9.5208 | 12.6045 | 16.297 | 20.7376 | 23.2664 | 14.4207
3786 | 23.5097 | 20.5363 | 16.0747 | 10.896 | 6.9916 | 5.4861 | 6.2951 | 9.4402 | 12.5087 | 16.194 | 20.734 | 23.1442 | 14.3176
3787 | 23.5826 | 20.7204 | 16.2699 | 10.9354 | 7.0345 | 5.6342 | 6.3815 | 9.5911 | 12.6003 | 16.4494 | 20.856 | 23.3354 | 14.4492
3788 | 23.8134 | 20.8057 | 16.3509 | 10.982 | 7.0649 | 5.6219 | 6.3333 | 9.6262 | 12.6055 | 16.5309 | 21.064 | 23.3583 | 14.5131
3789 | 23.5097 | 20.5363 | 16.0747 | 10.896 | 6.9916 | 5.4861 | 6.2951 | 9.4402 | 12.5087 | 16.194 | 20.734 | 23.1442 | 14.3176
3791 | 23.8019 | 20.6958 | 16.2048 | 10.9467 | 7.1798 | 5.719 | 6.3739 | 9.5512 | 12.5958 | 16.5339 | 21.012 | 23.3617 | 14.498
3792 | 23.5671 | 20.5895 | 16.0809 | 10.9303 | 7.1054 | 5.5898 | 6.3017 | 9.5489 | 12.5065 | 16.4905 | 20.906 | 23.1878 | 14.4004
3793 | 23.8657 | 20.8677 | 16.3557 | 11.0085 | 7.1264 | 5.6873 | 6.3146 | 9.6044 | 12.4981 | 16.5547 | 21.0179 | 23.4892 | 14.5325
3795 | 23.8657 | 20.8677 | 16.3557 | 11.0085 | 7.1264 | 5.6873 | 6.3146 | 9.6044 | 12.4981 | 16.5547 | 21.0179 | 23.4892 | 14.5325
3796 | 23.855 | 20.9887 | 16.626 | 11.0685 | 7.1012 | 5.6926 | 6.4069 | 9.6714 | 12.5866 | 16.6239 | 21.0676 | 23.6059 | 14.6078
3797 | 23.2847 | 20.3066 | 15.8023 | 10.8089 | 6.9748 | 5.3882 | 5.9526 | 9.0981 | 12.1232 | 15.9667 | 20.0163 | 22.592 | 14.0262
3799 | 23.9838 | 20.9691 | 16.5284 | 11.2342 | 7.3045 | 5.4387 | 5.9382 | 9.1694 | 12.7702 | 16.756 | 20.7523 | 23.7647 | 14.5508
3800 | 23.7623 | 20.8211 | 16.713 | 11.0958 | 7.2855 | 5.8967 | 6.7898 | 9.7681 | 12.8506 | 17.0256 | 21.25 | 23.8818 | 14.7617
3802 | 23.5092 | 20.7839 | 16.4123 | 10.9433 | 7.218 | 5.8872 | 6.7496 | 9.7223 | 12.8184 | 16.5929 | 21.0668 | 23.5344 | 14.6032
3803 | 23.5515 | 20.7817 | 16.5148 | 10.9561 | 7.1871 | 5.9217 | 6.7644 | 9.9386 | 12.9609 | 16.7931 | 21.1497 | 23.6524 | 14.681
3804 | 23.4012 | 20.4299 | 16.0305 | 10.8566 | 7.037 | 5.5115 | 6.3772 | 9.4363 | 12.5575 | 16.1149 | 20.549 | 22.8662 | 14.264
3805 | 23.6031 | 20.833 | 16.4539 | 10.9286 | 7.1618 | 5.9228 | 6.7308 | 9.8832 | 12.9039 | 16.8337 | 21.0647 | 23.4103 | 14.6441
3806 | 23.5547 | 20.6746 | 16.3406 | 10.8561 | 7.1929 | 5.8941 | 6.6553 | 9.7871 | 12.855 | 16.7257 | 20.7943 | 23.2073 | 14.5448
3807 | 23.4518 | 20.4819 | 16.2168 | 10.8881 | 7.2062 | 5.8704 | 6.6378 | 9.6844 | 12.7618 | 16.4946 | 20.6261 | 22.9318 | 14.4376
3808 | 23.391 | 20.3778 | 16.165 | 10.8747 | 7.1654 | 5.7451 | 6.5418 | 9.6388 | 12.6694 | 16.4704 | 20.4972 | 22.8537 | 14.3659
3809 | 23.4518 | 20.4819 | 16.2168 | 10.8881 | 7.2062 | 5.8704 | 6.6378 | 9.6844 | 12.7618 | 16.4946 | 20.6261 | 22.9318 | 14.4376
3810 | 23.5902 | 20.5768 | 16.2354 | 10.8782 | 7.2284 | 5.8247 | 6.6353 | 9.6851 | 12.7183 | 16.5916 | 20.6264 | 22.9169 | 14.4589
3812 | 23.5028 | 20.6051 | 16.0893 | 10.9272 | 7.2298 | 5.8387 | 6.6298 | 9.6518 | 12.8773 | 16.529 | 20.4424 | 22.8741 | 14.4331
3813 | 23.2408 | 20.1911 | 15.978 | 10.8469 | 7.2758 | 5.919 | 6.5808 | 9.6988 | 12.6986 | 16.3427 | 20.1919 | 22.5974 | 14.2968
3814 | 23.7235 | 20.5205 | 16.1276 | 10.8415 | 7.3795 | 6.0542 | 6.7326 | 9.8826 | 12.7003 | 16.5787 | 20.6708 | 22.86 | 14.506
3815 | 23.7235 | 20.5205 | 16.1276 | 10.8415 | 7.3795 | 6.0542 | 6.7326 | 9.8826 | 12.7003 | 16.5787 | 20.6708 | 22.86 | 14.506
3816 | 23.2439 | 20.1878 | 15.8173 | 10.8454 | 7.311 | 5.9363 | 6.4868 | 9.5851 | 12.5179 | 16.122 | 19.8151 | 22.2093 | 14.1732
3818 | 24.0397 | 20.6459 | 16.3165 | 10.8869 | 7.1562 | 5.8852 | 6.6909 | 9.8903 | 12.7366 | 16.8411 | 20.8944 | 23.4082 | 14.616
3820 | 23.8717 | 20.783 | 16.3693 | 10.9874 | 7.3594 | 6.0497 | 6.7108 | 10 | 12.8102 | 16.9011 | 20.6845 | 23.3706 | 14.6581
3821 | 23.5335 | 20.379 | 16.333 | 11.0945 | 7.4732 | 6.0064 | 6.7124 | 10.0139 | 13.0578 | 16.9257 | 20.4264 | 22.9419 | 14.5748
3822 | 23.9434 | 20.751 | 16.3353 | 10.9032 | 7.336 | 5.9755 | 6.6603 | 10.0965 | 12.8944 | 16.9946 | 20.9028 | 23.6681 | 14.7051
3823 | 23.935 | 20.7272 | 16.4377 | 10.9126 | 7.2757 | 5.9288 | 6.6785 | 10.0483 | 13.0024 | 17.1917 | 21.0494 | 23.6975 | 14.7404
3824 | 23.8528 | 20.6963 | 16.4133 | 11.136 | 7.3843 | 6.0443 | 6.7843 | 10.2309 | 13.2897 | 17.2158 | 21.0882 | 23.8191 | 14.8296
3825 | 22.896 | 20.1569 | 16.0525 | 11.2616 | 7.6964 | 6.2941 | 6.9987 | 10.3991 | 13.4952 | 17.3875 | 20.3242 | 23.0297 | 14.666
3831 | 23.5549 | 20.2862 | 16.1886 | 11.1264 | 7.3882 | 5.9616 | 6.5967 | 9.877 | 13.2787 | 16.6533 | 20.152 | 22.9091 | 14.4977
3832 | 23.2983 | 20.3142 | 16.051 | 11.0467 | 7.4029 | 5.8924 | 6.4426 | 9.6645 | 13.1249 | 16.485 | 20.2005 | 22.7861 | 14.3924
3833 | 23.4322 | 20.661 | 15.9912 | 11.2105 | 7.4298 | 5.5618 | 6.0752 | 9.3067 | 12.9703 | 16.6443 | 20.6768 | 23.8001 | 14.48
3835 | 23.4222 | 20.4561 | 16.4164 | 11.1117 | 7.2045 | 5.7632 | 6.6576 | 10.0771 | 13.2642 | 17.2171 | 20.9673 | 23.6362 | 14.6828
3840 | 23.1336 | 20.2289 | 16.154 | 11.1322 | 7.539 | 6.17 | 6.9078 | 10.4016 | 13.4555 | 17.3977 | 20.5996 | 23.5927 | 14.7261
3842 | 23.1972 | 20.1863 | 16.1521 | 10.9532 | 7.3558 | 6.1161 | 6.8367 | 10.2399 | 13.3286 | 17.2485 | 20.7877 | 23.844 | 14.6872
3844 | 23.4361 | 20.5253 | 16.1888 | 11.231 | 7.6135 | 6.3336 | 7.1477 | 10.6185 | 13.6552 | 18.0211 | 21.2799 | 23.8665 | 14.9931
3847 | 23.6489 | 20.5947 | 16.4532 | 11.4001 | 7.7159 | 6.4163 | 7.3118 | 10.487 | 13.9493 | 17.8602 | 21.4433 | 23.8 | 15.0901
3850 | 24.0036 | 21.0187 | 17.1083 | 11.9537 | 8.1045 | 6.5532 | 7.6101 | 11.1162 | 14.4034 | 18.9498 | 22.3536 | 24.3726 | 15.629
3851 | 23.7514 | 20.7695 | 17.1098 | 11.8793 | 8.0428 | 6.4968 | 7.5229 | 10.7869 | 14.3466 | 18.6286 | 22.0635 | 23.9505 | 15.4457
3852 | 23.9128 | 21.0004 | 17.2674 | 12.0034 | 8.0734 | 6.5799 | 7.6216 | 11.0714 | 14.553 | 18.9352 | 22.1474 | 24.1105 | 15.6064
3854 | 23.3448 | 20.1432 | 16.5829 | 11.7117 | 8.2111 | 6.665 | 7.429 | 10.8598 | 13.6433 | 18.0672 | 21.2502 | 23.8304 | 15.1449
3856 | 22.7079 | 20.0937 | 16.5245 | 11.6932 | 8.0987 | 6.4988 | 7.3022 | 10.7062 | 13.9477 | 17.8788 | 20.9878 | 23.5704 | 15.0008
3857 | 23.7749 | 20.6123 | 17.0198 | 11.8778 | 8.2618 | 6.7972 | 7.5464 | 10.9112 | 13.959 | 18.4404 | 21.8507 | 24.1736 | 15.4354
3858 | 22.7968 | 20.4624 | 17.0834 | 12.0572 | 8.0282 | 6.1767 | 6.9766 | 10.4699 | 14.1674 | 18.0976 | 21.0114 | 24.3339 | 15.1385
3859 | 23.6092 | 20.5073 | 17.0609 | 12.0567 | 8.3987 | 6.8112 | 7.72 | 11.0453 | 14.1309 | 18.6565 | 21.6357 | 24.0561 | 15.474
3860 | 22.9814 | 19.995 | 16.7699 | 12.0081 | 8.2705 | 6.7381 | 7.7414 | 10.9645 | 13.9995 | 18.0552 | 21.0011 | 23.5088 | 15.1695
3862 | 21.9595 | 19.8286 | 16.5866 | 11.9448 | 8.074 | 6.6202 | 7.5817 | 11.2259 | 14.3727 | 17.8446 | 20.4858 | 23.4988 | 15.0019
3864 | 22.621 | 19.831 | 16.6331 | 12.0695 | 8.3333 | 6.7815 | 7.6985 | 11.1015 | 14.1246 | 18.0043 | 20.78 | 23.0469 | 15.0854
3865 | 22.946 | 19.9959 | 16.7196 | 12.0309 | 8.3082 | 6.7486 | 7.7024 | 10.9729 | 14.0211 | 17.8548 | 21.145 | 23.2249 | 15.1392
3869 | 23.3345 | 20.2316 | 16.1829 | 10.9344 | 7.2637 | 6.0648 | 6.7459 | 10.1226 | 13.2211 | 17.2851 | 21.0897 | 23.7161 | 14.6827
3870 | 23.0171 | 20.065 | 15.828 | 10.6561 | 6.9607 | 5.8554 | 6.6033 | 9.8094 | 12.9398 | 17.0507 | 20.7364 | 23.5159 | 14.4198
3871 | 23.1647 | 20.2048 | 15.8344 | 10.8304 | 7.0703 | 6.0528 | 6.6448 | 9.795 | 12.7699 | 16.7539 | 20.7474 | 23.4132 | 14.4401
3873 | 23.2097 | 20.2588 | 16.3262 | 11.2591 | 7.5192 | 6.1178 | 6.9774 | 10.4739 | 13.8705 | 17.9986 | 21.3244 | 23.8329 | 14.9307
3874 | 23.547 | 20.3433 | 16.3071 | 11.2999 | 7.5795 | 6.3547 | 7.1913 | 10.3384 | 13.645 | 17.7579 | 21.3414 | 23.5425 | 14.9373
3875 | 23.5917 | 20.4342 | 16.8009 | 11.9955 | 8.2715 | 6.7491 | 7.7839 | 11.0806 | 14.169 | 18.3282 | 21.6368 | 23.484 | 15.3605
3878 | 23.4185 | 20.4731 | 17.1005 | 12.0313 | 8.1577 | 6.539 | 7.6041 | 11.0941 | 14.3042 | 18.5183 | 21.7305 | 23.2981 | 15.3558
3880 | 23.9919 | 20.9033 | 17.5122 | 12.2014 | 8.2008 | 6.5433 | 7.7248 | 11.2244 | 14.6906 | 18.7627 | 22.2507 | 23.7648 | 15.6476
3882 | 22.9762 | 20.2301 | 16.5323 | 11.9435 | 8.2428 | 6.7105 | 7.6921 | 10.9772 | 13.9469 | 17.96 | 21.1868 | 23.136 | 15.1279
3885 | 22.6868 | 20.4979 | 17.2567 | 12.4175 | 8.2515 | 6.6245 | 7.6368 | 11.2809 | 14.7905 | 18.8141 | 21.1106 | 24.5689 | 15.4947
3886 | 23.0586 | 20.5761 | 16.5893 | 11.7494 | 8.1412 | 6.6457 | 7.6475 | 11.0109 | 14.0622 | 18.1089 | 21.2838 | 22.8623 | 15.1447
3887 | 22.4383 | 19.7344 | 16.278 | 11.9479 | 8.2596 | 6.6333 | 7.6411 | 11.0464 | 14.0798 | 17.9119 | 20.9851 | 22.6477 | 14.967
3888 | 21.7132 | 19.5017 | 15.9479 | 11.7187 | 7.8813 | 6.4933 | 7.4562 | 10.9584 | 13.8324 | 17.3037 | 20.4225 | 22.2276 | 14.6214
3889 | 21.2482 | 19.6958 | 15.9098 | 11.8552 | 7.9922 | 6.7547 | 7.6736 | 11.1082 | 14.2646 | 17.4251 | 20.2083 | 22.022 | 14.6798
3890 | 21.626 | 19.7289 | 15.9536 | 11.7738 | 7.9665 | 6.7857 | 7.748 | 11.0143 | 14.1563 | 17.5204 | 20.2892 | 22.1019 | 14.722
3891 | 21.7955 | 19.9362 | 16.653 | 12.1255 | 8.2477 | 6.9092 | 7.8599 | 11.1072 | 14.4766 | 18.0342 | 20.9513 | 22.3733 | 15.0391
3892 | 22.3959 | 20.3994 | 17.0917 | 12.1032 | 8.1368 | 6.7894 | 7.8271 | 11.1856 | 14.6943 | 18.4016 | 21.5732 | 22.8678 | 15.2888
3895 | 22.4127 | 20.1214 | 16.821 | 12.0381 | 8.119 | 6.7633 | 7.7555 | 11.4974 | 14.5638 | 18.2608 | 21.3042 | 23.825 | 15.2902
3896 | 23.3611 | 20.713 | 17.7435 | 12.5723 | 8.5291 | 6.8502 | 7.8296 | 11.4222 | 14.5663 | 18.7794 | 21.903 | 25.0904 | 15.78
3898 | 24.3905 | 21.8285 | 18.3337 | 12.8877 | 8.7234 | 7.0288 | 8.0069 | 11.6341 | 14.8181 | 19.3861 | 22.6202 | 25.9469 | 16.3004
3900 | 25.3717 | 22.2915 | 18.9335 | 13.0797 | 8.3629 | 6.1313 | 7.3124 | 10.7049 | 14.3858 | 19.245 | 23.2081 | 26.5666 | 16.2994
3902 | 23.0384 | 20.3295 | 16.6039 | 11.843 | 8.2274 | 6.6895 | 7.7222 | 11.042 | 14.0034 | 18.0666 | 21.2643 | 23.2538 | 15.1737
3903 | 23.0322 | 20.3286 | 16.5671 | 11.8501 | 8.1982 | 6.6638 | 7.6648 | 11.0805 | 14.1605 | 18.0253 | 21.1692 | 23.1812 | 15.1601
3904 | 23.5336 | 20.6857 | 16.8121 | 11.8084 | 8.208 | 6.6341 | 7.6492 | 11.1142 | 14.3308 | 18.2918 | 21.6876 | 23.5345 | 15.3575
3909 | 23.3076 | 20.4331 | 16.8011 | 11.9884 | 8.2562 | 6.6737 | 7.7134 | 11.0594 | 14.3759 | 18.5487 | 21.5635 | 23.2341 | 15.3296
3910 | 24.0838 | 21.2184 | 16.752 | 11.0116 | 7.1829 | 6.0197 | 6.9029 | 10.3003 | 13.4777 | 17.7054 | 21.7064 | 24.1948 | 15.0463
3911 | 23.9952 | 21.2016 | 16.7788 | 10.9265 | 7.1735 | 6.0511 | 6.9246 | 10.3023 | 13.6 | 17.528 | 21.575 | 24.0395 | 15.008
3912 | 23.9952 | 21.2016 | 16.7788 | 10.9265 | 7.1735 | 6.0511 | 6.9246 | 10.3023 | 13.6 | 17.528 | 21.575 | 24.0395 | 15.008
3913 | 24.0875 | 21.1517 | 16.8292 | 10.9964 | 7.1533 | 6.0722 | 7.0193 | 10.3207 | 13.8028 | 17.4954 | 21.561 | 24.0024 | 15.041
3915 | 24.3116 | 21.2648 | 16.8384 | 11.007 | 7.1049 | 6.0929 | 6.9829 | 10.3896 | 13.6427 | 17.5886 | 21.765 | 24.317 | 15.1088
3916 | 24.4116 | 21.2992 | 16.9195 | 11.014 | 7.0065 | 5.9072 | 6.9721 | 10.2525 | 13.8706 | 17.8577 | 21.9625 | 24.333 | 15.1505
3918 | 23.887 | 20.912 | 16.8809 | 11.1641 | 7.1443 | 6.0157 | 6.9919 | 10.359 | 14.1262 | 17.6941 | 21.6045 | 24.0565 | 15.0697
3919 | 23.887 | 20.912 | 16.8809 | 11.1641 | 7.1443 | 6.0157 | 6.9919 | 10.359 | 14.1262 | 17.6941 | 21.6045 | 24.0565 | 15.0697
3920 | 23.9187 | 20.9432 | 16.9364 | 11.197 | 7.1289 | 6.0146 | 6.9595 | 10.2756 | 13.9722 | 17.8891 | 21.8673 | 24.3648 | 15.1223
3921 | 23.7879 | 20.6574 | 16.5876 | 11.1905 | 7.1534 | 6.0476 | 6.9306 | 10.1748 | 13.481 | 17.4327 | 21.5275 | 24.0041 | 14.9146
3922 | 24.2786 | 21.3096 | 16.9878 | 11.1344 | 7.2129 | 6.0459 | 6.9185 | 10.1096 | 13.8774 | 18.2133 | 22.3336 | 24.6424 | 15.2553
3923 | 24.2723 | 21.275 | 17.0406 | 11.1846 | 7.2104 | 6.0046 | 6.8841 | 10.1822 | 13.8301 | 18.107 | 22.1876 | 24.5253 | 15.2253
3925 | 24.4003 | 21.4187 | 17.0968 | 11.1579 | 7.2035 | 5.9562 | 6.8872 | 10.1832 | 13.8451 | 18.3476 | 22.4633 | 24.9855 | 15.3288
3926 | 24.2149 | 21.2425 | 16.8859 | 10.97 | 7.1155 | 6.0057 | 6.9393 | 10.2546 | 13.8267 | 17.7756 | 21.802 | 24.3455 | 15.1148
3927 | 24.1316 | 21.1713 | 16.9588 | 11.1636 | 7.1247 | 5.9686 | 7.007 | 10.3028 | 14 | 17.9941 | 21.9608 | 24.4197 | 15.1836
3928 | 24.3376 | 21.0773 | 16.7408 | 11.1926 | 7.0995 | 5.9393 | 6.9257 | 10.0662 | 13.5318 | 17.7514 | 21.8418 | 24.4654 | 15.0808
3929 | 24.239 | 21.378 | 16.8337 | 11.0442 | 6.9793 | 5.8619 | 6.9563 | 10.1488 | 13.8715 | 17.9523 | 21.9154 | 24.273 | 15.1211
3930 | 24.0346 | 20.886 | 16.7861 | 11.1843 | 7.2911 | 6.0842 | 7.0213 | 10.2976 | 13.4417 | 17.6858 | 21.9077 | 24.4168 | 15.0864
3931 | 24.2657 | 21.034 | 16.8922 | 11.2051 | 7.2603 | 6.0805 | 7.0429 | 10.2947 | 13.3741 | 17.6934 | 21.824 | 24.5516 | 15.1265
3933 | 24.258 | 21.0456 | 16.6039 | 11.0412 | 7.1778 | 6.0857 | 7.0351 | 10.2752 | 13.4904 | 17.5874 | 21.725 | 24.2899 | 15.0513
3934 | 24.2657 | 21.034 | 16.8922 | 11.2051 | 7.2603 | 6.0805 | 7.0429 | 10.2947 | 13.3741 | 17.6934 | 21.824 | 24.5516 | 15.1265
3936 | 24.4068 | 21.0204 | 16.8273 | 11.135 | 7.1213 | 5.9714 | 6.9527 | 10.1941 | 13.469 | 17.751 | 21.9418 | 24.3848 | 15.098
3937 | 24.4116 | 21.2992 | 16.9195 | 11.014 | 7.0065 | 5.9072 | 6.9721 | 10.2525 | 13.8706 | 17.8577 | 21.9625 | 24.333 | 15.1505
3938 | 24.3376 | 21.0773 | 16.7408 | 11.1926 | 7.0995 | 5.9393 | 6.9257 | 10.0662 | 13.5318 | 17.7514 | 21.8418 | 24.4654 | 15.0808
3939 | 24.3036 | 21.1768 | 16.8509 | 11.3315 | 7.2263 | 6.0253 | 6.9695 | 10.081 | 13.5282 | 17.8836 | 22.0856 | 24.8402 | 15.1919
3940 | 24.3036 | 21.1768 | 16.8509 | 11.3315 | 7.2263 | 6.0253 | 6.9695 | 10.081 | 13.5282 | 17.8836 | 22.0856 | 24.8402 | 15.1919
3941 | 24.5054 | 21.4723 | 17.2189 | 11.6108 | 7.3762 | 6.1078 | 6.9755 | 10.1995 | 13.6503 | 18.381 | 22.4434 | 25.2715 | 15.4344
3942 | 24.6834 | 21.5958 | 17.5089 | 11.7863 | 7.4483 | 6.0756 | 6.9863 | 10.3689 | 13.9049 | 18.5024 | 22.4835 | 25.3405 | 15.5571
3943 | 24.6834 | 21.5958 | 17.5089 | 11.7863 | 7.4483 | 6.0756 | 6.9863 | 10.3689 | 13.9049 | 18.5024 | 22.4835 | 25.3405 | 15.5571
3944 | 24.5439 | 21.519 | 17.4533 | 11.6516 | 7.3664 | 6.0396 | 6.9726 | 10.3491 | 13.9435 | 18.5263 | 22.4998 | 25.2897 | 15.5129
3945 | 23.9277 | 20.8775 | 16.3821 | 10.7785 | 6.896 | 5.7921 | 6.574 | 9.9082 | 12.6618 | 16.8076 | 21.0735 | 23.8005 | 14.6233
3950 | 23.7426 | 20.6772 | 16.2993 | 10.6412 | 6.8274 | 5.727 | 6.5337 | 9.7956 | 12.6621 | 16.6586 | 20.9251 | 23.5364 | 14.5022
3951 | 23.9379 | 20.8446 | 16.3701 | 10.7505 | 6.9255 | 5.7602 | 6.6586 | 9.7868 | 12.8931 | 16.9726 | 21.2989 | 23.7527 | 14.6626
3953 | 23.4795 | 20.5658 | 16.0408 | 10.7827 | 6.8766 | 5.6994 | 6.5245 | 9.6885 | 12.7178 | 16.6919 | 20.6871 | 23.2734 | 14.419
3954 | 23.7916 | 20.7235 | 16.129 | 10.7331 | 7.0621 | 6.0023 | 6.774 | 9.9704 | 13.0147 | 17.2594 | 21.1951 | 23.5446 | 14.6833
3956 | 24.5293 | 21.5177 | 16.6417 | 10.6275 | 7.0753 | 5.9143 | 6.6999 | 10.0315 | 13.5736 | 18.0862 | 22.5345 | 24.9615 | 15.1828
3957 | 23.4898 | 20.4159 | 16.0304 | 10.603 | 6.977 | 5.8672 | 6.6505 | 9.763 | 12.744 | 16.9615 | 20.9759 | 23.3997 | 14.4898
3958 | 23.9994 | 20.8403 | 16.2082 | 10.6732 | 7.0009 | 5.9302 | 6.6471 | 9.9718 | 13.0555 | 17.428 | 21.5833 | 23.8963 | 14.7695
3959 | 24.0003 | 20.9007 | 16.1883 | 10.4605 | 6.9271 | 5.7442 | 6.5197 | 9.6948 | 13.2281 | 17.3559 | 21.5447 | 23.5639 | 14.6774
3960 | 23.8553 | 20.7535 | 16.0716 | 10.688 | 6.922 | 5.7708 | 6.695 | 9.8351 | 13.4417 | 17.9625 | 21.803 | 24.3879 | 14.8489
3962 | 22.9868 | 20.2091 | 15.7969 | 10.5222 | 7.0517 | 5.779 | 6.5229 | 9.5666 | 12.9154 | 16.9482 | 20.7185 | 22.8965 | 14.3262
3965 | 23.34 | 20.58 | 16.2508 | 10.8886 | 7.251 | 6.1107 | 6.9892 | 10.1529 | 13.638 | 17.7745 | 21.4125 | 23.5721 | 14.83
3966 | 22.7404 | 20.0195 | 15.6414 | 10.6514 | 7.2146 | 5.8554 | 6.6905 | 9.7666 | 13.1879 | 17.1311 | 20.9701 | 22.9449 | 14.4011
3971 | 23.0766 | 20.0366 | 16.0422 | 10.9774 | 7.5235 | 6.1993 | 6.9593 | 10.0582 | 13.5141 | 17.637 | 20.8679 | 23.3559 | 14.6873
3975 | 23.6963 | 20.9247 | 16.5215 | 11.0109 | 7.2605 | 5.9935 | 6.7951 | 10.0045 | 13.0544 | 17.0663 | 21.2633 | 23.7652 | 14.7797
3976 | 23.6963 | 20.9247 | 16.5215 | 11.0109 | 7.2605 | 5.9935 | 6.7951 | 10.0045 | 13.0544 | 17.0663 | 21.2633 | 23.7652 | 14.7797
3977 | 23.9824 | 21.0972 | 16.6276 | 10.9749 | 7.2241 | 6.0062 | 6.8836 | 10.1261 | 13.3726 | 17.435 | 21.3109 | 23.8497 | 14.9075
3978 | 23.9104 | 20.9989 | 16.5211 | 10.918 | 7.1774 | 6.0005 | 6.8751 | 10.0423 | 13.1221 | 17.1279 | 21.369 | 23.8521 | 14.8262
3979 | 24.3794 | 21.1332 | 16.5107 | 10.7841 | 6.9044 | 5.8308 | 6.7831 | 9.9474 | 12.995 | 17.1845 | 21.5991 | 24.153 | 14.8504
3980 | 23.9139 | 21.0336 | 16.7624 | 10.9917 | 7.1459 | 6.0266 | 6.9201 | 10.2762 | 13.3235 | 17.3638 | 21.5035 | 24.0612 | 14.9435
3981 | 23.8714 | 20.7175 | 16.5518 | 11.0163 | 7.249 | 6.0045 | 6.779 | 9.8773 | 12.8778 | 17.1292 | 21.2025 | 23.5904 | 14.7389
3984 | 24.2483 | 21.0961 | 16.584 | 11.0296 | 7.2146 | 6.0184 | 6.8865 | 10.025 | 12.9569 | 17.3276 | 21.5059 | 24.2233 | 14.9263
3987 | 24.0884 | 20.8974 | 16.4883 | 10.8678 | 7.0357 | 5.9369 | 6.7421 | 9.9892 | 12.8761 | 17.2352 | 21.3211 | 24.0593 | 14.7948
3988 | 23.9498 | 20.6104 | 16.3218 | 10.7602 | 6.9388 | 5.8248 | 6.6908 | 9.8327 | 12.7113 | 16.97 | 20.9725 | 23.7396 | 14.6102
3991 | 24.4371 | 21.1975 | 16.5643 | 10.8803 | 7.0223 | 5.9918 | 6.8787 | 10.0872 | 13.1169 | 17.8041 | 21.9729 | 24.6242 | 15.0481
3992 | 24.4951 | 21.41 | 16.5805 | 10.7759 | 6.9246 | 5.8185 | 6.7801 | 10.0297 | 13.2347 | 17.6436 | 21.9606 | 24.6616 | 15.0262
3995 | 24.4487 | 21.3496 | 16.6979 | 10.6308 | 6.8958 | 5.8734 | 6.7478 | 9.9859 | 13.4732 | 17.7628 | 21.8025 | 24.4801 | 15.0124
3996 | 24.1874 | 21.0528 | 16.6016 | 10.68 | 6.9393 | 5.9354 | 6.7508 | 9.9835 | 13.2434 | 17.6528 | 21.5973 | 24.1736 | 14.8998
4000 | 23.801 | 20.8941 | 19.7415 | 16.4559 | 13.2839 | 11.8833 | 13.2599 | 16.1252 | 20.1353 | 21.5604 | 23.273 | 24.6359 | 18.7541
4005 | 24.2502 | 21.3042 | 20.1574 | 16.5811 | 13.3271 | 11.9155 | 13.3445 | 16.3609 | 20.3728 | 21.7635 | 23.4786 | 24.9624 | 18.9849
4006 | 24.2502 | 21.3042 | 20.1574 | 16.5811 | 13.3271 | 11.9155 | 13.3445 | 16.3609 | 20.3728 | 21.7635 | 23.4786 | 24.9624 | 18.9849
4007 | 24.2502 | 21.3042 | 20.1574 | 16.5811 | 13.3271 | 11.9155 | 13.3445 | 16.3609 | 20.3728 | 21.7635 | 23.4786 | 24.9624 | 18.9849
4008 | 25.1017 | 21.8174 | 20.9184 | 16.9003 | 13.2303 | 11.8681 | 13.4545 | 16.5102 | 20.7307 | 21.7781 | 23.6986 | 25.3739 | 19.2818
4009 | 24.895 | 21.7702 | 20.713 | 16.7834 | 13.2905 | 11.905 | 13.4396 | 16.5908 | 20.6372 | 21.807 | 23.6406 | 25.2151 | 19.2239
4010 | 24.2502 | 21.3042 | 20.1574 | 16.5811 | 13.3271 | 11.9155 | 13.3445 | 16.3609 | 20.3728 | 21.7635 | 23.4786 | 24.9624 | 18.9849
4011 | 24.5636 | 21.6186 | 20.4095 | 16.6393 | 13.278 | 11.9079 | 13.4043 | 16.4132 | 20.6152 | 21.781 | 23.446 | 25.1446 | 19.1018
4012 | 24.5636 | 21.6186 | 20.4095 | 16.6393 | 13.278 | 11.9079 | 13.4043 | 16.4132 | 20.6152 | 21.781 | 23.446 | 25.1446 | 19.1018
4013 | 24.5636 | 21.6186 | 20.4095 | 16.6393 | 13.278 | 11.9079 | 13.4043 | 16.4132 | 20.6152 | 21.781 | 23.446 | 25.1446 | 19.1018
4014 | 25.1017 | 21.8174 | 20.9184 | 16.9003 | 13.2303 | 11.8681 | 13.4545 | 16.5102 | 20.7307 | 21.7781 | 23.6986 | 25.3739 | 19.2818
4017 | 24.9426 | 21.9783 | 21.1763 | 17.0699 | 13.3045 | 11.8854 | 13.4372 | 16.6017 | 21.0213 | 22.0081 | 24.011 | 25.389 | 19.4021
4018 | 24.7086 | 21.6736 | 20.7901 | 16.8486 | 13.2789 | 11.8931 | 13.3986 | 16.4613 | 20.9019 | 21.8974 | 23.6159 | 25.2786 | 19.2289
4019 | 25.6294 | 22.2127 | 21.4885 | 17.3266 | 13.4539 | 12.0234 | 13.5919 | 16.7407 | 21.1443 | 22.3112 | 24.4762 | 25.9964 | 19.6996
4020 | 25.659 | 22.2816 | 21.6058 | 17.3518 | 13.4847 | 12.0166 | 13.6179 | 16.7174 | 21.3022 | 22.3557 | 24.8489 | 26.076 | 19.7765
4021 | 25.6294 | 22.2127 | 21.4885 | 17.3266 | 13.4539 | 12.0234 | 13.5919 | 16.7407 | 21.1443 | 22.3112 | 24.4762 | 25.9964 | 19.6996
4022 | 25.0791 | 21.9743 | 21.2616 | 17.0591 | 13.3687 | 11.9593 | 13.4282 | 16.4569 | 21.0175 | 22.005 | 24.0485 | 25.5013 | 19.43
4025 | 25.5616 | 22.8089 | 21.1462 | 16.6622 | 13.0483 | 11.6173 | 13.3526 | 16.5541 | 21.0433 | 22.2843 | 24.6178 | 26.1335 | 19.5692
4030 | 24.5636 | 21.6186 | 20.4095 | 16.6393 | 13.278 | 11.9079 | 13.4043 | 16.4132 | 20.6152 | 21.781 | 23.446 | 25.1446 | 19.1018
4031 | 24.5636 | 21.6186 | 20.4095 | 16.6393 | 13.278 | 11.9079 | 13.4043 | 16.4132 | 20.6152 | 21.781 | 23.446 | 25.1446 | 19.1018
4032 | 23.9862 | 21.1328 | 20.0137 | 16.4556 | 13.2944 | 11.9461 | 13.3143 | 16.176 | 20.3966 | 21.6573 | 23.3208 | 24.8506 | 18.8787
4034 | 24.7086 | 21.6736 | 20.7901 | 16.8486 | 13.2789 | 11.8931 | 13.3986 | 16.4613 | 20.9019 | 21.8974 | 23.6159 | 25.2786 | 19.2289
4035 | 23.6519 | 20.722 | 19.8285 | 16.3989 | 13.2059 | 11.9601 | 13.3007 | 15.9721 | 20.247 | 21.4609 | 23.1438 | 24.6856 | 18.7148
4036 | 24.4897 | 21.4788 | 20.5483 | 16.7516 | 13.3423 | 11.979 | 13.3833 | 16.4507 | 20.825 | 21.8544 | 23.691 | 25.0732 | 19.1556
4037 | 23.6519 | 20.722 | 19.8285 | 16.3989 | 13.2059 | 11.9601 | 13.3007 | 15.9721 | 20.247 | 21.4609 | 23.1438 | 24.6856 | 18.7148
4051 | 23.801 | 20.8941 | 19.7415 | 16.4559 | 13.2839 | 11.8833 | 13.2599 | 16.1252 | 20.1353 | 21.5604 | 23.273 | 24.6359 | 18.7541
4053 | 23.9862 | 21.1328 | 20.0137 | 16.4556 | 13.2944 | 11.9461 | 13.3143 | 16.176 | 20.3966 | 21.6573 | 23.3208 | 24.8506 | 18.8787
4054 | 23.369 | 20.6564 | 19.7169 | 16.3799 | 13.224 | 11.8621 | 13.2335 | 15.9705 | 20.0084 | 21.2809 | 22.9666 | 24.3921 | 18.5884
4055 | 23.369 | 20.6564 | 19.7169 | 16.3799 | 13.224 | 11.8621 | 13.2335 | 15.9705 | 20.0084 | 21.2809 | 22.9666 | 24.3921 | 18.5884
4059 | 23.801 | 20.8941 | 19.7415 | 16.4559 | 13.2839 | 11.8833 | 13.2599 | 16.1252 | 20.1353 | 21.5604 | 23.273 | 24.6359 | 18.7541
4060 | 23.801 | 20.8941 | 19.7415 | 16.4559 | 13.2839 | 11.8833 | 13.2599 | 16.1252 | 20.1353 | 21.5604 | 23.273 | 24.6359 | 18.7541
4061 | 23.2647 | 20.4558 | 19.5541 | 16.2974 | 13.1963 | 11.8191 | 13.1747 | 15.9419 | 19.8753 | 21.1308 | 22.9445 | 24.2334 | 18.4907
4064 | 23.801 | 20.8941 | 19.7415 | 16.4559 | 13.2839 | 11.8833 | 13.2599 | 16.1252 | 20.1353 | 21.5604 | 23.273 | 24.6359 | 18.7541
4065 | 23.801 | 20.8941 | 19.7415 | 16.4559 | 13.2839 | 11.8833 | 13.2599 | 16.1252 | 20.1353 | 21.5604 | 23.273 | 24.6359 | 18.7541
4066 | 23.272 | 20.4348 | 19.5945 | 16.2854 | 13.1589 | 11.8147 | 13.1518 | 15.8821 | 19.7557 | 21.2309 | 22.9459 | 24.298 | 18.4854
4067 | 23.689 | 20.7333 | 19.7159 | 16.4089 | 13.2379 | 11.848 | 13.2703 | 16.095 | 19.9436 | 21.4768 | 23.2433 | 24.5688 | 18.6859
4068 | 23.689 | 20.7333 | 19.7159 | 16.4089 | 13.2379 | 11.848 | 13.2703 | 16.095 | 19.9436 | 21.4768 | 23.2433 | 24.5688 | 18.6859
4069 | 23.0218 | 20.2474 | 19.5439 | 16.2747 | 13.1321 | 11.7626 | 13.1521 | 15.7355 | 19.6544 | 21.0204 | 22.6168 | 23.9201 | 18.3402
4070 | 23.4329 | 20.5768 | 19.6768 | 16.4277 | 13.2429 | 11.8061 | 13.2257 | 15.888 | 19.7204 | 21.248 | 22.8181 | 24.3121 | 18.5313
4072 | 23.689 | 20.7333 | 19.7159 | 16.4089 | 13.2379 | 11.848 | 13.2703 | 16.095 | 19.9436 | 21.4768 | 23.2433 | 24.5688 | 18.6859
4073 | 23.5897 | 20.6352 | 19.6889 | 16.3811 | 13.2066 | 11.808 | 13.2125 | 15.9136 | 19.7798 | 21.3494 | 22.9921 | 24.4143 | 18.5809
4074 | 23.4329 | 20.5768 | 19.6768 | 16.4277 | 13.2429 | 11.8061 | 13.2257 | 15.888 | 19.7204 | 21.248 | 22.8181 | 24.3121 | 18.5313
4075 | 23.7922 | 20.8162 | 19.9303 | 16.359 | 13.2419 | 11.8606 | 13.273 | 16.0539 | 19.9154 | 21.5411 | 23.156 | 24.5156 | 18.7046
4076 | 23.7445 | 20.7226 | 19.9002 | 16.5836 | 13.3072 | 11.8615 | 13.2743 | 16.0476 | 19.8039 | 21.3921 | 23.0819 | 24.6106 | 18.6942
4077 | 23.8546 | 20.7458 | 19.8893 | 16.558 | 13.2259 | 11.84 | 13.2871 | 16.1009 | 19.7708 | 21.3886 | 23.1025 | 24.6081 | 18.6976
4078 | 23.8546 | 20.7458 | 19.8893 | 16.558 | 13.2259 | 11.84 | 13.2871 | 16.1009 | 19.7708 | 21.3886 | 23.1025 | 24.6081 | 18.6976
4101 | 23.689 | 20.7333 | 19.7159 | 16.4089 | 13.2379 | 11.848 | 13.2703 | 16.095 | 19.9436 | 21.4768 | 23.2433 | 24.5688 | 18.6859
4102 | 24.0807 | 21.0808 | 20.0182 | 16.537 | 13.258 | 11.889 | 13.3085 | 16.1849 | 20.223 | 21.6636 | 23.4823 | 24.8731 | 18.8833
4103 | 24.0807 | 21.0808 | 20.0182 | 16.537 | 13.258 | 11.889 | 13.3085 | 16.1849 | 20.223 | 21.6636 | 23.4823 | 24.8731 | 18.8833
4104 | 23.689 | 20.7333 | 19.7159 | 16.4089 | 13.2379 | 11.848 | 13.2703 | 16.095 | 19.9436 | 21.4768 | 23.2433 | 24.5688 | 18.6859
4105 | 23.7922 | 20.8162 | 19.9303 | 16.359 | 13.2419 | 11.8606 | 13.273 | 16.0539 | 19.9154 | 21.5411 | 23.156 | 24.5156 | 18.7046
4106 | 23.7922 | 20.8162 | 19.9303 | 16.359 | 13.2419 | 11.8606 | 13.273 | 16.0539 | 19.9154 | 21.5411 | 23.156 | 24.5156 | 18.7046
4107 | 24.1086 | 21.1456 | 20.1327 | 16.4986 | 13.2627 | 11.8654 | 13.3109 | 16.1614 | 20.1196 | 21.65 | 23.3967 | 24.8336 | 18.8738
4108 | 24.1086 | 21.1456 | 20.1327 | 16.4986 | 13.2627 | 11.8654 | 13.3109 | 16.1614 | 20.1196 | 21.65 | 23.3967 | 24.8336 | 18.8738
4109 | 24.087 | 20.9715 | 20.2708 | 16.5883 | 13.3018 | 11.8505 | 13.2236 | 16.1451 | 20.1081 | 21.5157 | 23.2481 | 24.9015 | 18.851
4110 | 24.0192 | 20.8301 | 20.0186 | 16.5245 | 13.2446 | 11.888 | 13.2595 | 16.1472 | 19.8914 | 21.477 | 23.1617 | 24.5867 | 18.754
4111 | 24.1086 | 21.1456 | 20.1327 | 16.4986 | 13.2627 | 11.8654 | 13.3109 | 16.1614 | 20.1196 | 21.65 | 23.3967 | 24.8336 | 18.8738
4112 | 24.1346 | 21.1682 | 20.3819 | 16.6412 | 13.3147 | 11.8083 | 13.1967 | 16.2325 | 20.2416 | 21.5702 | 23.2352 | 24.9636 | 18.9074
4113 | 24.1346 | 21.1682 | 20.3819 | 16.6412 | 13.3147 | 11.8083 | 13.1967 | 16.2325 | 20.2416 | 21.5702 | 23.2352 | 24.9636 | 18.9074
4114 | 24.1836 | 21.209 | 20.4012 | 16.5935 | 13.3151 | 11.7823 | 13.1856 | 16.2219 | 20.1718 | 21.5101 | 23.2253 | 25.0124 | 18.901
4115 | 24.1146 | 21.0403 | 20.2141 | 16.5436 | 13.2671 | 11.8177 | 13.2148 | 16.1952 | 20.1456 | 21.5783 | 23.2345 | 24.928 | 18.8578
4116 | 24.1146 | 21.0403 | 20.2141 | 16.5436 | 13.2671 | 11.8177 | 13.2148 | 16.1952 | 20.1456 | 21.5783 | 23.2345 | 24.928 | 18.8578
4117 | 24.1836 | 21.209 | 20.4012 | 16.5935 | 13.3151 | 11.7823 | 13.1856 | 16.2219 | 20.1718 | 21.5101 | 23.2253 | 25.0124 | 18.901
4118 | 24.1146 | 21.0403 | 20.2141 | 16.5436 | 13.2671 | 11.8177 | 13.2148 | 16.1952 | 20.1456 | 21.5783 | 23.2345 | 24.928 | 18.8578
4119 | 24.1346 | 21.1682 | 20.3819 | 16.6412 | 13.3147 | 11.8083 | 13.1967 | 16.2325 | 20.2416 | 21.5702 | 23.2352 | 24.9636 | 18.9074
4120 | 24.0807 | 21.0808 | 20.0182 | 16.537 | 13.258 | 11.889 | 13.3085 | 16.1849 | 20.223 | 21.6636 | 23.4823 | 24.8731 | 18.8833
4121 | 24.0807 | 21.0808 | 20.0182 | 16.537 | 13.258 | 11.889 | 13.3085 | 16.1849 | 20.223 | 21.6636 | 23.4823 | 24.8731 | 18.8833
4122 | 24.2771 | 21.3337 | 20.3218 | 16.6967 | 13.3345 | 11.8755 | 13.2972 | 16.2861 | 20.3195 | 21.6966 | 23.427 | 24.994 | 18.9883
4123 | 24.3604 | 21.3148 | 20.5406 | 16.7322 | 13.3428 | 11.8231 | 13.2316 | 16.2325 | 20.2743 | 21.6796 | 23.4557 | 25.12 | 19.009
4124 | 23.7236 | 20.8463 | 19.9776 | 16.6442 | 13.2803 | 11.8372 | 13.2217 | 16.1347 | 19.881 | 21.3279 | 22.9849 | 24.5731 | 18.7027
4125 | 24.0123 | 20.9564 | 20.0336 | 16.5463 | 13.2417 | 11.8225 | 13.2113 | 16.1611 | 20.0654 | 21.5536 | 23.2145 | 24.9327 | 18.8126
4127 | 24.3522 | 21.328 | 20.507 | 16.7137 | 13.282 | 11.7894 | 13.1753 | 16.2249 | 20.1809 | 21.4721 | 23.2383 | 25.1387 | 18.9502
4128 | 24.4779 | 21.4901 | 20.5889 | 16.731 | 13.28 | 11.8335 | 13.2397 | 16.3811 | 20.2483 | 21.718 | 23.4669 | 25.2013 | 19.0547
4129 | 24.4668 | 21.4031 | 20.4919 | 16.7073 | 13.2256 | 11.7753 | 13.2328 | 16.2481 | 20.0933 | 21.6345 | 23.347 | 25.1416 | 18.9806
4130 | 24.8438 | 21.8156 | 20.8185 | 16.854 | 13.1939 | 11.7705 | 13.3412 | 16.5554 | 20.5923 | 22.0302 | 23.6144 | 25.3701 | 19.2333
4131 | 24.3522 | 21.328 | 20.507 | 16.7137 | 13.282 | 11.7894 | 13.1753 | 16.2249 | 20.1809 | 21.4721 | 23.2383 | 25.1387 | 18.9502
4132 | 24.1337 | 21.1215 | 20.2225 | 16.5688 | 13.2212 | 11.7592 | 13.1723 | 16.1735 | 20.0782 | 21.5141 | 23.2662 | 25.0524 | 18.857
4133 | 24.0391 | 21.093 | 20.1873 | 16.5308 | 13.2305 | 11.7615 | 13.1489 | 16.0762 | 20.0077 | 21.4618 | 23.2379 | 25.0121 | 18.8156
4151 | 24.0807 | 21.0808 | 20.0182 | 16.537 | 13.258 | 11.889 | 13.3085 | 16.1849 | 20.223 | 21.6636 | 23.4823 | 24.8731 | 18.8833
4152 | 24.5443 | 21.4702 | 20.3827 | 16.7561 | 13.3241 | 11.8911 | 13.4007 | 16.3885 | 20.458 | 21.7716 | 23.5813 | 25.0959 | 19.0887
4153 | 25.0766 | 22.0065 | 20.8515 | 16.929 | 13.3299 | 11.9062 | 13.4621 | 16.5635 | 20.6013 | 21.8178 | 23.706 | 25.3402 | 19.2992
4154 | 25.0766 | 22.0065 | 20.8515 | 16.929 | 13.3299 | 11.9062 | 13.4621 | 16.5635 | 20.6013 | 21.8178 | 23.706 | 25.3402 | 19.2992
4155 | 25.0766 | 22.0065 | 20.8515 | 16.929 | 13.3299 | 11.9062 | 13.4621 | 16.5635 | 20.6013 | 21.8178 | 23.706 | 25.3402 | 19.2992
4156 | 24.6466 | 21.6361 | 20.6003 | 16.8206 | 13.3738 | 11.8436 | 13.3684 | 16.4523 | 20.4485 | 21.8573 | 23.7045 | 25.161 | 19.1594
4157 | 25.0931 | 22.0101 | 20.9066 | 16.9091 | 13.3038 | 11.8269 | 13.4159 | 16.5721 | 20.4785 | 21.8581 | 23.8004 | 25.4617 | 19.303
4158 | 25.2874 | 22.0579 | 21.2103 | 17.1258 | 13.3188 | 11.8569 | 13.4744 | 16.6451 | 20.7475 | 21.9975 | 24.001 | 25.6372 | 19.4467
4159 | 25.2874 | 22.0579 | 21.2103 | 17.1258 | 13.3188 | 11.8569 | 13.4744 | 16.6451 | 20.7475 | 21.9975 | 24.001 | 25.6372 | 19.4467
4160 | 25.7306 | 22.2871 | 21.6358 | 17.3993 | 13.4339 | 11.9505 | 13.6434 | 16.9644 | 21.0459 | 22.5887 | 24.5479 | 26.1485 | 19.7813
4161 | 25.3874 | 22.2049 | 21.1895 | 17.1938 | 13.2586 | 11.8337 | 13.4271 | 16.7259 | 20.7334 | 22.0584 | 23.9475 | 25.7105 | 19.4726
4163 | 25.3874 | 22.2049 | 21.1895 | 17.1938 | 13.2586 | 11.8337 | 13.4271 | 16.7259 | 20.7334 | 22.0584 | 23.9475 | 25.7105 | 19.4726
4164 | 25.3874 | 22.2049 | 21.1895 | 17.1938 | 13.2586 | 11.8337 | 13.4271 | 16.7259 | 20.7334 | 22.0584 | 23.9475 | 25.7105 | 19.4726
4165 | 24.8438 | 21.8156 | 20.8185 | 16.854 | 13.1939 | 11.7705 | 13.3412 | 16.5554 | 20.5923 | 22.0302 | 23.6144 | 25.3701 | 19.2333
4169 | 24.0807 | 21.0808 | 20.0182 | 16.537 | 13.258 | 11.889 | 13.3085 | 16.1849 | 20.223 | 21.6636 | 23.4823 | 24.8731 | 18.8833
4170 | 24.895 | 21.7702 | 20.713 | 16.7834 | 13.2905 | 11.905 | 13.4396 | 16.5908 | 20.6372 | 21.807 | 23.6406 | 25.2151 | 19.2239
4171 | 24.2502 | 21.3042 | 20.1574 | 16.5811 | 13.3271 | 11.9155 | 13.3445 | 16.3609 | 20.3728 | 21.7635 | 23.4786 | 24.9624 | 18.9849
4172 | 24.895 | 21.7702 | 20.713 | 16.7834 | 13.2905 | 11.905 | 13.4396 | 16.5908 | 20.6372 | 21.807 | 23.6406 | 25.2151 | 19.2239
4173 | 25.3305 | 22.1153 | 21.155 | 17.101 | 13.2854 | 11.9075 | 13.497 | 16.7476 | 20.8728 | 21.8808 | 23.8109 | 25.4462 | 19.4292
4174 | 25.3305 | 22.1153 | 21.155 | 17.101 | 13.2854 | 11.9075 | 13.497 | 16.7476 | 20.8728 | 21.8808 | 23.8109 | 25.4462 | 19.4292
4178 | 25.3305 | 22.1153 | 21.155 | 17.101 | 13.2854 | 11.9075 | 13.497 | 16.7476 | 20.8728 | 21.8808 | 23.8109 | 25.4462 | 19.4292
4179 | 25.3305 | 22.1153 | 21.155 | 17.101 | 13.2854 | 11.9075 | 13.497 | 16.7476 | 20.8728 | 21.8808 | 23.8109 | 25.4462 | 19.4292
4183 | 25.5626 | 22.2389 | 20.8977 | 16.4629 | 12.9742 | 11.6608 | 13.2638 | 16.5669 | 20.5345 | 22.1941 | 24.3351 | 25.9591 | 19.3876
4184 | 25.5348 | 22.2009 | 21.05 | 16.763 | 12.9735 | 11.6819 | 13.2849 | 16.6195 | 20.6379 | 22.0889 | 24.2243 | 25.7885 | 19.404
4205 | 24.2867 | 21.2974 | 20.3872 | 16.6632 | 13.1773 | 11.7298 | 13.1706 | 16.199 | 20.0864 | 21.5056 | 23.2676 | 25.1831 | 18.9128
4207 | 24.1248 | 21.0652 | 20.0785 | 16.5832 | 13.185 | 11.6338 | 13.1174 | 16.0542 | 19.8557 | 21.5181 | 23.2945 | 24.9442 | 18.7879
4208 | 25.2445 | 22.0172 | 20.9824 | 16.9831 | 12.9743 | 11.5734 | 13.1858 | 16.4534 | 20.6568 | 21.9827 | 23.9341 | 25.5991 | 19.2989
4209 | 24.5529 | 21.5977 | 20.6832 | 16.7709 | 13.0787 | 11.6647 | 13.1501 | 16.3763 | 20.5473 | 21.7956 | 23.532 | 25.2942 | 19.087
4210 | 23.8374 | 20.7729 | 19.9774 | 16.4633 | 13.0383 | 11.6347 | 13.0538 | 16.0435 | 20.0534 | 21.2978 | 22.9493 | 24.5417 | 18.6386
4211 | 22.7832 | 20.015 | 19.2585 | 16.2233 | 12.7702 | 11.4961 | 12.9103 | 15.7401 | 19.5821 | 20.7023 | 22.2664 | 23.7596 | 18.1256
4212 | 25.2568 | 21.9246 | 21.0065 | 16.9796 | 12.9638 | 11.6744 | 13.2331 | 16.4854 | 20.5312 | 22.0467 | 24.0451 | 25.589 | 19.3114
4213 | 22.7898 | 19.6938 | 18.9245 | 16.2525 | 12.8111 | 11.489 | 12.8626 | 15.5054 | 19.3407 | 20.6577 | 21.9296 | 23.489 | 17.9788
4214 | 24.8525 | 21.6113 | 20.814 | 16.8426 | 12.9716 | 11.6891 | 13.1688 | 16.2898 | 20.6269 | 21.6713 | 23.3808 | 25.3255 | 19.1037
4215 | 25.4088 | 22.0436 | 21.1504 | 17.0988 | 12.9303 | 11.5688 | 13.1466 | 16.4609 | 20.8649 | 21.8483 | 23.8785 | 25.6054 | 19.3338
4216 | 25.4537 | 22.16 | 21.2529 | 17.2028 | 12.9599 | 11.5171 | 13.1899 | 16.5079 | 20.907 | 22.0272 | 24.1905 | 25.8094 | 19.4315
4217 | 25.2119 | 21.9906 | 20.9579 | 17.0696 | 12.9657 | 11.557 | 13.0958 | 16.3465 | 20.8092 | 21.7204 | 23.4837 | 25.3068 | 19.2096
4218 | 24.7543 | 21.9118 | 20.6884 | 16.9584 | 12.9161 | 11.5447 | 13.0703 | 16.2172 | 20.6853 | 21.6279 | 23.1332 | 25.0555 | 19.0469
4219 | 24.8191 | 21.7015 | 20.6571 | 16.9228 | 12.8693 | 11.4993 | 13.0219 | 16.1021 | 20.5439 | 21.6946 | 23.4454 | 25.2207 | 19.0415
4220 | 24.8191 | 21.7015 | 20.6571 | 16.9228 | 12.8693 | 11.4993 | 13.0219 | 16.1021 | 20.5439 | 21.6946 | 23.4454 | 25.2207 | 19.0415
4221 | 24.8191 | 21.7015 | 20.6571 | 16.9228 | 12.8693 | 11.4993 | 13.0219 | 16.1021 | 20.5439 | 21.6946 | 23.4454 | 25.2207 | 19.0415
4223 | 23.153 | 20.4727 | 19.3062 | 16.2096 | 12.6954 | 11.4534 | 12.938 | 15.7463 | 19.7821 | 21.0049 | 22.433 | 23.9932 | 18.2657
4224 | 25.0695 | 21.9073 | 20.6129 | 16.9516 | 12.8772 | 11.5498 | 13.1333 | 16.3133 | 20.564 | 21.9622 | 23.7174 | 25.5384 | 19.1831
4225 | 25.0695 | 21.9073 | 20.6129 | 16.9516 | 12.8772 | 11.5498 | 13.1333 | 16.3133 | 20.564 | 21.9622 | 23.7174 | 25.5384 | 19.1831
4226 | 24.7543 | 21.9118 | 20.6884 | 16.9584 | 12.9161 | 11.5447 | 13.0703 | 16.2172 | 20.6853 | 21.6279 | 23.1332 | 25.0555 | 19.0469
4227 | 24.3773 | 21.5832 | 20.2216 | 16.6352 | 12.8546 | 11.567 | 13.0434 | 16.0131 | 20.4374 | 21.4346 | 22.8129 | 24.7939 | 18.8145
4228 | 22.5334 | 19.8456 | 18.8744 | 16.0287 | 12.73 | 11.4104 | 12.8878 | 15.5884 | 19.4628 | 20.664 | 21.9727 | 23.3804 | 17.9482
4229 | 24.3773 | 21.5832 | 20.2216 | 16.6352 | 12.8546 | 11.567 | 13.0434 | 16.0131 | 20.4374 | 21.4346 | 22.8129 | 24.7939 | 18.8145
4230 | 24.3773 | 21.5832 | 20.2216 | 16.6352 | 12.8546 | 11.567 | 13.0434 | 16.0131 | 20.4374 | 21.4346 | 22.8129 | 24.7939 | 18.8145
4270 | 23.973 | 20.9388 | 19.9578 | 16.6073 | 13.1354 | 11.6321 | 13.0672 | 15.9715 | 19.8209 | 21.4103 | 23.1915 | 24.8627 | 18.714
4271 | 23.9274 | 20.7653 | 19.875 | 16.5961 | 13.0267 | 11.6415 | 13.064 | 15.9191 | 19.7583 | 21.249 | 23.0353 | 24.6179 | 18.623
4272 | 23.5982 | 20.5301 | 19.5401 | 16.3983 | 12.8675 | 11.5228 | 12.9988 | 15.8238 | 19.6089 | 21.1009 | 22.6689 | 24.2618 | 18.41
4275 | 22.7052 | 19.7248 | 18.1279 | 15.9592 | 12.5209 | 11.0641 | 12.5173 | 15.288 | 19.111 | 20.4487 | 21.6875 | 23.2849 | 17.7033
4280 | 23.8077 | 20.8634 | 19.9314 | 16.5112 | 13.1702 | 11.7475 | 13.1541 | 15.9502 | 19.8166 | 21.372 | 22.9756 | 24.748 | 18.6707
4285 | 23.9447 | 20.9757 | 19.612 | 16.5988 | 13.1105 | 11.6335 | 13.1323 | 15.893 | 19.8019 | 21.5133 | 23.0089 | 24.7915 | 18.668
4287 | 23.9736 | 20.9603 | 19.9279 | 16.8195 | 13.3066 | 11.5755 | 13.0487 | 16.0265 | 19.9075 | 21.3543 | 22.7588 | 24.6949 | 18.6962
4300 | 23.8411 | 20.7207 | 19.9742 | 16.7144 | 13.3316 | 11.8838 | 13.28 | 16.2196 | 19.9397 | 21.5202 | 23.1361 | 24.8149 | 18.7814
4301 | 23.8873 | 20.892 | 20.1009 | 16.6659 | 13.3345 | 11.9152 | 13.2579 | 16.163 | 19.9508 | 21.4355 | 23.251 | 24.8377 | 18.8076
4303 | 23.8276 | 20.7364 | 19.8992 | 16.5541 | 13.2961 | 11.8388 | 13.2512 | 16.0863 | 19.8674 | 21.3394 | 23.1711 | 24.8051 | 18.7227
4304 | 23.8413 | 20.7652 | 19.9958 | 16.5821 | 13.3349 | 11.8259 | 13.2904 | 16.1675 | 19.9573 | 21.406 | 23.2434 | 24.9358 | 18.7788
4305 | 23.8455 | 20.7597 | 20.0372 | 16.6838 | 13.3859 | 11.8815 | 13.2678 | 16.1849 | 20.0568 | 21.558 | 23.2926 | 24.9837 | 18.8281
4306 | 23.1762 | 20.1484 | 19.4539 | 16.0217 | 13.1426 | 11.5981 | 13.0698 | 15.9859 | 19.7192 | 21.2154 | 23.0373 | 24.3168 | 18.4071
4307 | 24.1137 | 21.1687 | 20.1377 | 16.837 | 13.4204 | 11.9635 | 13.2778 | 16.1957 | 20.0015 | 21.6923 | 23.2626 | 24.9697 | 18.92
4309 | 23.625 | 20.297 | 19.6008 | 16.6049 | 13.2039 | 11.6039 | 12.9091 | 15.8702 | 19.7381 | 21.2392 | 22.4781 | 24.3625 | 18.4611
4310 | 24.3543 | 21.5217 | 20.1302 | 16.885 | 13.4108 | 11.6923 | 13.1751 | 16.159 | 20.0636 | 21.5941 | 23.0854 | 24.9337 | 18.9171
4311 | 24.2558 | 21.1492 | 20.2349 | 16.9336 | 13.4532 | 12.0133 | 13.3395 | 16.2713 | 20.1741 | 21.7977 | 23.6417 | 25.2151 | 19.04
4312 | 23.678 | 20.6148 | 19.4938 | 16.1734 | 13.2123 | 11.7083 | 13.1392 | 16.039 | 20.0128 | 21.5079 | 23.3459 | 24.8225 | 18.6457
4313 | 23.9504 | 20.6442 | 19.9694 | 16.6266 | 13.4059 | 12.0817 | 13.38 | 16.2685 | 20.1376 | 21.425 | 23.3149 | 24.621 | 18.8188
4340 | 24.194 | 20.8884 | 20.313 | 16.8942 | 13.451 | 11.9958 | 13.307 | 16.2873 | 20.1004 | 21.8399 | 23.4456 | 25.0939 | 18.9842
4341 | 24.3249 | 20.945 | 20.4146 | 17.0015 | 13.5538 | 12.0463 | 13.3423 | 16.2441 | 20.1298 | 21.8722 | 23.7234 | 25.4378 | 19.0863
4342 | 24.1321 | 20.8947 | 20.1429 | 16.712 | 13.3842 | 12.0574 | 13.3065 | 16.2561 | 20.1947 | 21.7309 | 23.7072 | 25.1135 | 18.9693
4343 | 24.2847 | 20.744 | 20.143 | 16.9259 | 13.4287 | 11.9117 | 13.1051 | 16.1206 | 20.0178 | 21.621 | 23.3783 | 24.9895 | 18.8892
4344 | 24.7533 | 21.1248 | 20.5033 | 17.0298 | 13.4745 | 11.9801 | 13.2085 | 16.3478 | 20.1687 | 21.8805 | 23.7723 | 25.412 | 19.138
4345 | 24.2085 | 20.8088 | 20.1935 | 16.8113 | 13.4001 | 11.9996 | 13.3309 | 16.2374 | 20.1243 | 21.6466 | 23.6009 | 25.0665 | 18.9524
4346 | 24.2855 | 21.0564 | 20.177 | 16.7514 | 13.3783 | 12.0291 | 13.4092 | 16.3735 | 20.2754 | 21.8487 | 23.6855 | 25.1679 | 19.0365
4347 | 24.6453 | 20.9711 | 20.3923 | 17.0206 | 13.4213 | 11.9821 | 13.1552 | 16.3665 | 20.1115 | 21.9691 | 23.8583 | 25.4793 | 19.1144
4350 | 25.6925 | 21.9482 | 20.902 | 17.4578 | 13.6488 | 12.1355 | 12.9878 | 16.493 | 20.3257 | 22.5935 | 24.3765 | 26.2908 | 19.571
4352 | 25.847 | 22.5388 | 20.8874 | 17.4721 | 13.5617 | 11.779 | 12.9165 | 16.3607 | 19.908 | 22.1403 | 24.0273 | 26.59 | 19.5024
4353 | 24.6473 | 20.9866 | 20.2661 | 17.0368 | 13.3885 | 11.9889 | 13.0855 | 16.3264 | 20.1247 | 22.0586 | 23.735 | 25.283 | 19.0773
4354 | 25.1833 | 21.5492 | 20.7358 | 17.162 | 13.658 | 12.0254 | 13.0904 | 16.454 | 20.2866 | 22.3262 | 24.2721 | 25.7649 | 19.3757
4355 | 24.4124 | 20.7379 | 20.1145 | 16.8996 | 13.3797 | 12.0587 | 13.2251 | 16.2792 | 20.0834 | 21.765 | 23.4855 | 24.9071 | 18.9457
4356 | 25.6861 | 22.4765 | 21.0106 | 17.4389 | 13.8229 | 12.1808 | 13.1273 | 16.4916 | 20.2159 | 22.3848 | 24.3697 | 26.402 | 19.6339
4357 | 25.6821 | 22.6647 | 21.2985 | 17.6878 | 13.6866 | 11.9693 | 13.0509 | 16.5526 | 20.4438 | 22.2519 | 24.3357 | 26.428 | 19.671
4358 | 25.3622 | 21.9372 | 20.6943 | 17.2397 | 13.6699 | 11.9694 | 12.9328 | 16.3779 | 20.234 | 22.3905 | 24.3955 | 26.1196 | 19.4436
4359 | 25.0335 | 21.5247 | 20.5067 | 17.0715 | 13.4626 | 11.8744 | 12.8576 | 16.3173 | 20.1496 | 22.269 | 24.0161 | 25.8279 | 19.2426
4360 | 25.3017 | 21.787 | 20.4187 | 17.1049 | 13.5673 | 11.9189 | 12.9234 | 16.413 | 20.0358 | 22.3957 | 24.407 | 26.1311 | 19.367
4361 | 25.0916 | 21.6381 | 20.2465 | 17.0843 | 13.5468 | 11.8778 | 12.8901 | 16.2333 | 19.8234 | 22.2397 | 24.1649 | 25.8292 | 19.2221
4362 | 25.202 | 21.9221 | 20.2431 | 17.0733 | 13.507 | 11.8095 | 12.9162 | 16.2176 | 19.9156 | 21.9307 | 24.0269 | 25.8106 | 19.2145
4363 | 25.4134 | 22.0346 | 20.7501 | 17.2243 | 13.6698 | 12.0346 | 12.9771 | 16.4858 | 20.339 | 22.4669 | 24.3603 | 26.2629 | 19.5016
4364 | 25.6538 | 22.1064 | 21.0409 | 17.581 | 13.7655 | 12.076 | 13.0824 | 16.5227 | 20.1224 | 22.2588 | 24.3126 | 26.1706 | 19.5578
4365 | 25.7972 | 22.6174 | 21.112 | 17.6524 | 13.7334 | 11.9618 | 13.0262 | 16.4207 | 20.1759 | 22.19 | 24.2517 | 26.5534 | 19.6243
4370 | 25.3914 | 22.4124 | 20.4505 | 17.2813 | 13.5221 | 11.7332 | 12.9167 | 16.3377 | 19.9861 | 21.9892 | 23.9574 | 26.0581 | 19.3363
4371 | 23.9783 | 20.5986 | 19.2053 | 16.4705 | 12.8334 | 11.3666 | 12.5187 | 15.8048 | 19.4284 | 21.2949 | 22.9431 | 24.629 | 18.4226
4372 | 24.6039 | 21.3621 | 19.417 | 16.7316 | 13.101 | 11.4665 | 12.6767 | 16.0935 | 19.8079 | 21.8049 | 23.4067 | 25.4204 | 18.8243
4373 | 23.6847 | 20.3359 | 18.3527 | 16.0109 | 12.5683 | 11.1336 | 12.3575 | 15.7005 | 19.4591 | 21.25 | 22.7352 | 24.4018 | 18.1658
4374 | 24.9628 | 21.9001 | 20.1879 | 17.1383 | 13.2077 | 11.6337 | 12.7881 | 16.2571 | 19.9652 | 21.8964 | 23.5725 | 25.968 | 19.1231
4375 | 24.7496 | 21.694 | 19.7147 | 16.7476 | 13.086 | 11.4424 | 12.5438 | 16.1045 | 19.6632 | 21.6804 | 23.1566 | 25.5513 | 18.8445
4376 | 24.6983 | 21.5508 | 19.5766 | 16.6705 | 12.9906 | 11.3583 | 12.5073 | 16.0435 | 19.5905 | 21.6757 | 23.1343 | 25.4817 | 18.7732
4377 | 24.6426 | 21.4023 | 19.4299 | 16.474 | 12.9237 | 11.3121 | 12.4248 | 15.9654 | 19.5383 | 21.7671 | 23.2069 | 25.3972 | 18.707
4378 | 24.6426 | 21.4023 | 19.4299 | 16.474 | 12.9237 | 11.3121 | 12.4248 | 15.9654 | 19.5383 | 21.7671 | 23.2069 | 25.3972 | 18.707
4380 | 25.4928 | 22.3375 | 20.6892 | 16.99 | 13.1597 | 11.378 | 12.3736 | 16.0912 | 19.638 | 22.0153 | 23.7606 | 26.3526 | 19.1899
4381 | 24.7915 | 21.3848 | 19.6603 | 16.6443 | 12.9466 | 11.1916 | 12.2562 | 15.9029 | 19.4033 | 21.6446 | 23.0019 | 25.6373 | 18.7054
4382 | 25.0436 | 21.6433 | 19.8651 | 16.6067 | 12.8719 | 11.1615 | 12.154 | 15.8309 | 19.3379 | 21.582 | 22.9546 | 25.562 | 18.7178
4383 | 24.6464 | 21.1181 | 19.3977 | 16.5635 | 12.6977 | 10.9962 | 12.0885 | 15.5173 | 19.3249 | 21.3477 | 22.5531 | 25.3376 | 18.4657
4385 | 26.5498 | 23.2025 | 21.366 | 17.4103 | 13.4772 | 11.5831 | 12.6434 | 16.1607 | 20.0658 | 22.4252 | 24.6756 | 27.0935 | 19.7211
4387 | 26.0998 | 22.8974 | 21.2651 | 17.4127 | 13.5677 | 11.8261 | 12.8177 | 16.3578 | 19.9124 | 22.1034 | 24.4535 | 26.5978 | 19.6093
4388 | 26.731 | 23.5068 | 21.9169 | 17.8075 | 13.8056 | 11.9402 | 12.9011 | 16.5582 | 20.4805 | 22.7028 | 25.0535 | 27.3239 | 20.0607
4390 | 26.7541 | 23.635 | 22.0128 | 17.9664 | 14.0079 | 12.1043 | 13.0218 | 16.6257 | 20.6845 | 22.7344 | 25.1144 | 27.3222 | 20.1653
4400 | 25.6691 | 21.9583 | 21.0457 | 17.5986 | 13.7141 | 12.1006 | 13.0783 | 16.5246 | 20.3553 | 22.526 | 24.2558 | 26.1698 | 19.583
4401 | 25.6303 | 22.2191 | 21.1926 | 17.5817 | 13.8535 | 12.1373 | 13.1645 | 16.6008 | 20.3657 | 22.5008 | 24.4063 | 26.4068 | 19.6716
4402 | 24.4222 | 21.0088 | 20.3326 | 16.8821 | 13.4629 | 11.9914 | 13.093 | 16.3468 | 20.363 | 21.8263 | 23.6342 | 25.1209 | 19.0404
4403 | 25.7677 | 22.3622 | 21.3186 | 17.6542 | 13.901 | 12.2421 | 13.1661 | 16.5896 | 20.3689 | 22.5092 | 24.5415 | 26.4485 | 19.7391
4404 | 25.7481 | 22.4368 | 21.3967 | 17.5641 | 14.0088 | 12.3354 | 13.357 | 16.6394 | 20.5692 | 22.4904 | 24.6504 | 26.6374 | 19.8195
4405 | 26.1899 | 22.6764 | 21.5803 | 17.6243 | 14.1417 | 12.3302 | 13.3879 | 16.893 | 20.7658 | 22.3774 | 24.6217 | 26.7264 | 19.9429
4406 | 26.2133 | 22.7962 | 21.6897 | 17.9153 | 14.0917 | 12.238 | 13.2879 | 16.7618 | 20.8419 | 22.5904 | 24.865 | 26.8988 | 20.0158
4407 | 25.7089 | 22.1487 | 21.2992 | 17.5593 | 13.9167 | 12.1636 | 13.1195 | 16.6229 | 20.5746 | 22.3269 | 24.3385 | 26.3003 | 19.6733
4408 | 25.3933 | 22.2159 | 21.1697 | 17.36 | 14.1555 | 12.3069 | 13.4979 | 16.923 | 20.7285 | 22.5824 | 24.6696 | 26.2541 | 19.7714
4410 | 25.3943 | 22.3293 | 21.3672 | 17.2966 | 14.2696 | 12.4622 | 13.6332 | 16.9675 | 20.9419 | 22.5442 | 24.616 | 26.4646 | 19.8572
4411 | 25.7158 | 22.6783 | 21.7181 | 17.5505 | 14.3166 | 12.4288 | 13.5726 | 16.9859 | 20.9689 | 22.5811 | 24.9819 | 26.66 | 20.0132
4412 | 26.1797 | 23.1948 | 21.9812 | 17.6151 | 14.4778 | 12.5701 | 13.6556 | 17.0258 | 21.1447 | 22.7842 | 25.0256 | 27.0007 | 20.2213
4413 | 25.047 | 22.3862 | 21.6461 | 17.4766 | 14.3517 | 12.6312 | 13.7342 | 17.1304 | 21.2012 | 22.4734 | 24.4554 | 26.0594 | 19.8827
4415 | 25.9872 | 22.6676 | 22.216 | 18.0205 | 14.5148 | 12.7307 | 13.8964 | 17.3026 | 21.3734 | 22.829 | 24.7426 | 26.7017 | 20.2485
4416 | 26.3163 | 23.2989 | 22.198 | 18.0362 | 14.5408 | 12.6307 | 13.8081 | 17.1627 | 21.4191 | 22.8774 | 24.9565 | 26.9912 | 20.353
4417 | 26.648 | 23.6235 | 22.4482 | 18.2516 | 14.6205 | 12.5854 | 13.8599 | 17.1799 | 21.4429 | 23.2982 | 25.283 | 27.3846 | 20.5521
4419 | 26.2768 | 23.1177 | 22.3245 | 18.1325 | 15.0182 | 13.2646 | 14.3653 | 17.6891 | 21.7432 | 23.1229 | 25.4935 | 26.7425 | 20.6076
4420 | 25.5576 | 22.8852 | 22.3208 | 18.2708 | 15.1473 | 13.3978 | 14.7755 | 17.7334 | 21.8127 | 23.0284 | 24.9229 | 25.9615 | 20.4845
4421 | 26.6332 | 23.5116 | 22.2439 | 18.0108 | 14.3603 | 12.4014 | 13.5584 | 16.9834 | 21.1507 | 22.7661 | 24.9292 | 27.2542 | 20.3169
4422 | 26.8202 | 23.6217 | 22.1953 | 18.1079 | 14.3886 | 12.462 | 13.6046 | 16.9214 | 21.1724 | 23.0054 | 25.3753 | 27.4447 | 20.4266
4424 | 26.2458 | 23.2254 | 22.3568 | 18.068 | 14.801 | 12.9365 | 14.0558 | 17.3638 | 21.3027 | 22.7441 | 25.0017 | 27.038 | 20.4283
4425 | 26.268 | 23.3809 | 22.4959 | 18.2849 | 14.697 | 12.7465 | 13.9368 | 17.3129 | 21.4194 | 22.9435 | 25.2542 | 27.0297 | 20.4808
4427 | 26.2949 | 23.3285 | 22.4713 | 18.2574 | 14.7776 | 12.8938 | 14.093 | 17.4973 | 21.534 | 23.0543 | 25.3255 | 26.7504 | 20.5232
4428 | 26.2675 | 23.395 | 22.4567 | 18.2728 | 14.6807 | 12.8155 | 14.0351 | 17.4056 | 21.6451 | 23.0997 | 25.2179 | 26.7426 | 20.5028
4454 | 25.917 | 23.1132 | 22.6658 | 18.474 | 15.4285 | 13.3576 | 14.6385 | 17.6675 | 21.5894 | 23.1846 | 25.0638 | 26.3214 | 20.6184
4455 | 26.5952 | 23.6387 | 22.7113 | 18.271 | 14.9025 | 12.8758 | 14.2139 | 17.4583 | 21.6515 | 23.3965 | 25.5125 | 26.9201 | 20.6789
4462 | 26.5049 | 23.3854 | 22.7539 | 18.3179 | 14.8469 | 12.9188 | 14.2457 | 17.5556 | 21.8472 | 23.4532 | 25.1742 | 26.9682 | 20.6643
4465 | 26.7038 | 23.6907 | 22.7944 | 18.4486 | 14.7712 | 12.6511 | 14.0331 | 17.4565 | 21.5197 | 23.3517 | 25.2625 | 27.1907 | 20.6562
4468 | 26.7663 | 23.6268 | 22.9797 | 18.486 | 14.7966 | 12.8278 | 14.3174 | 17.6081 | 21.4903 | 23.7323 | 25.3652 | 27.3421 | 20.7782
4470 | 26.597 | 24.2053 | 23.1494 | 18.6797 | 15.2306 | 13.2698 | 14.8084 | 18.0022 | 21.9843 | 24.0024 | 25.6155 | 27.2773 | 21.0685
4472 | 26.6603 | 25.0043 | 23.4498 | 19.3484 | 16.058 | 14.4641 | 15.8382 | 18.8649 | 22.5445 | 24.2522 | 25.8608 | 27.2413 | 21.6322
4477 | 26.0802 | 23.4358 | 22.7689 | 18.7114 | 15.3235 | 13.4372 | 14.8802 | 18.0187 | 21.8612 | 23.3587 | 25.0893 | 26.4756 | 20.7867
4478 | 26.1155 | 24.1998 | 22.9813 | 18.738 | 15.73 | 13.9814 | 15.4345 | 18.5534 | 22.4998 | 23.9449 | 25.4578 | 26.8846 | 21.2101
4480 | 27.1321 | 24.9402 | 23.7223 | 19.0889 | 15.2954 | 13.4232 | 14.8182 | 18.3581 | 22.0302 | 24.3652 | 26.3547 | 27.8577 | 21.4489
4481 | 27.4826 | 25.5724 | 23.9693 | 19.7964 | 16.0763 | 14.1444 | 15.4568 | 18.788 | 22.3996 | 24.8017 | 26.5622 | 27.6068 | 21.888
4486 | 26.9814 | 24.103 | 22.4378 | 17.668 | 14.0389 | 12.0605 | 13.3097 | 16.8817 | 20.914 | 23.2893 | 25.1181 | 28.0429 | 20.4038
4487 | 26.7958 | 23.6271 | 22.3642 | 18.1327 | 14.2383 | 12.1426 | 13.4928 | 16.9023 | 20.9314 | 23.1913 | 25.0686 | 27.5671 | 20.3712
4488 | 27.1585 | 24.1895 | 22.7952 | 17.7959 | 14.1488 | 12.2646 | 13.593 | 17.1026 | 21.1293 | 23.5775 | 25.4155 | 28.105 | 20.6063
4490 | 27.1997 | 24.6389 | 22.9667 | 18.0999 | 14.3585 | 12.4221 | 13.838 | 17.2864 | 21.2215 | 23.8466 | 25.6758 | 28.235 | 20.8158
4492 | 28.2822 | 25.339 | 23.5089 | 18.8569 | 14.6918 | 12.8484 | 13.9189 | 17.4671 | 21.019 | 24.2561 | 26.7025 | 28.7725 | 21.3053
4494 | 26.8957 | 23.8336 | 22.3078 | 17.9966 | 14.1814 | 12.0966 | 13.2422 | 16.7598 | 20.7177 | 23.0202 | 25.265 | 27.6604 | 20.3314
4496 | 26.9344 | 23.9303 | 22.4625 | 17.9614 | 14.0502 | 12.0887 | 13.1446 | 16.831 | 20.8543 | 23.2512 | 25.2299 | 27.701 | 20.37
4497 | 26.9769 | 23.9118 | 22.4717 | 17.8962 | 13.9552 | 11.9699 | 13.2039 | 16.8055 | 20.8607 | 23.2281 | 25.2011 | 27.9842 | 20.3721
4498 | 26.917 | 23.8965 | 22.2253 | 17.9702 | 14.0584 | 12.0215 | 13.1847 | 16.8071 | 20.6559 | 22.9522 | 25.1238 | 27.5771 | 20.2825
4500 | 23.8823 | 20.8332 | 20.0752 | 16.4853 | 13.2568 | 11.9409 | 13.2772 | 16.088 | 20.4195 | 21.6425 | 23.3994 | 24.8132 | 18.8428
4501 | 24.4897 | 21.4788 | 20.5483 | 16.7516 | 13.3423 | 11.979 | 13.3833 | 16.4507 | 20.825 | 21.8544 | 23.691 | 25.0732 | 19.1556
4502 | 23.8599 | 21.2025 | 20.2614 | 16.5477 | 13.2934 | 11.9489 | 13.254 | 16.2384 | 20.5519 | 21.7717 | 23.3714 | 24.7197 | 18.9184
4503 | 23.8599 | 21.2025 | 20.2614 | 16.5477 | 13.2934 | 11.9489 | 13.254 | 16.2384 | 20.5519 | 21.7717 | 23.3714 | 24.7197 | 18.9184
4504 | 23.1428 | 20.6559 | 19.9262 | 16.3733 | 13.2212 | 11.8592 | 13.2413 | 15.9901 | 20.2108 | 21.4353 | 23.0586 | 24.2531 | 18.614
4505 | 24.585 | 21.7804 | 20.8102 | 16.9503 | 13.3111 | 11.9245 | 13.4426 | 16.4822 | 20.8901 | 21.7003 | 23.6812 | 25.0443 | 19.2169
4506 | 24.1421 | 21.3807 | 20.442 | 16.6393 | 13.3006 | 11.912 | 13.4033 | 16.3431 | 20.5402 | 21.5651 | 23.362 | 24.756 | 18.9822
4507 | 25.3243 | 22.2034 | 21.1534 | 17.0009 | 13.3292 | 11.8867 | 13.5368 | 16.6785 | 21.2615 | 22.2693 | 24.6497 | 25.8712 | 19.5971
4508 | 24.578 | 21.82 | 20.7825 | 16.9364 | 13.3639 | 11.9559 | 13.4085 | 16.4885 | 20.9734 | 21.8 | 23.626 | 25.1537 | 19.2406
4509 | 25.0791 | 21.9743 | 21.2616 | 17.0591 | 13.3687 | 11.9593 | 13.4282 | 16.4569 | 21.0175 | 22.005 | 24.0485 | 25.5013 | 19.43
4510 | 23.8604 | 20.9784 | 20.3337 | 16.5848 | 13.3146 | 11.8194 | 13.3597 | 16.2253 | 20.2638 | 21.3825 | 23.2316 | 24.2731 | 18.8023
4511 | 24.6775 | 21.8155 | 20.9137 | 16.8513 | 13.2783 | 11.9089 | 13.5062 | 16.5337 | 20.8261 | 21.9606 | 24.2571 | 25.1877 | 19.3097
4512 | 22.6512 | 20.1592 | 19.5529 | 16.0577 | 13.1652 | 11.5829 | 13.036 | 15.8786 | 19.8975 | 20.9774 | 22.6196 | 23.6977 | 18.273
4514 | 22.3682 | 19.9767 | 19.0894 | 15.6683 | 12.9115 | 11.5239 | 12.9412 | 15.8611 | 19.8168 | 20.8022 | 22.4026 | 23.5122 | 18.0728
4515 | 23.3004 | 20.4965 | 19.752 | 16.0516 | 13.2396 | 11.8546 | 13.1922 | 16.0647 | 20.0888 | 21.2275 | 22.8454 | 24.126 | 18.5199
4516 | 23.4334 | 20.808 | 20.0888 | 16.355 | 13.2522 | 11.7645 | 13.2734 | 16.0797 | 20.2394 | 21.2638 | 23.1441 | 24.1334 | 18.653
4517 | 23.1413 | 20.6998 | 19.8661 | 16.2489 | 13.1719 | 11.7067 | 13.2231 | 16.0336 | 20.1328 | 21.143 | 23.0025 | 24.0271 | 18.5331
4518 | 22.5714 | 20.0694 | 19.223 | 15.992 | 12.9912 | 11.5919 | 13.139 | 15.8088 | 19.8751 | 20.9074 | 22.4194 | 23.5869 | 18.1813
4519 | 24.0117 | 21.3188 | 20.1916 | 16.4363 | 13.2077 | 11.8449 | 13.3339 | 16.2602 | 20.671 | 21.6615 | 23.5641 | 24.8256 | 18.9439
4520 | 22.6792 | 20.04 | 19.2785 | 15.9739 | 13.0254 | 11.6697 | 13.123 | 15.8357 | 19.8009 | 20.8311 | 22.2568 | 23.6803 | 18.1829
4521 | 22.6241 | 19.9082 | 19.2621 | 16.0313 | 13.1058 | 11.7244 | 13.1181 | 15.9311 | 19.7707 | 20.8799 | 22.3731 | 23.47 | 18.1832
4550 | 23.2743 | 20.933 | 19.8343 | 16.1588 | 13.228 | 11.8452 | 13.2961 | 16.0228 | 20.1649 | 21.202 | 23.0752 | 24.2288 | 18.6053
4551 | 24.8595 | 22.3149 | 20.7894 | 16.7445 | 13.3044 | 11.9173 | 13.454 | 16.5338 | 21.1144 | 21.9677 | 23.9252 | 25.3754 | 19.3584
4552 | 22.4932 | 20.0951 | 19.536 | 16.0083 | 13.1695 | 11.7625 | 13.0722 | 15.7851 | 19.817 | 20.8016 | 22.3888 | 23.6923 | 18.2185
4553 | 23.3974 | 20.9449 | 19.8657 | 16.2599 | 13.2448 | 11.8976 | 13.3818 | 16.0404 | 20.2822 | 21.3119 | 23.0373 | 24.3814 | 18.6704
4554 | 22.7077 | 20.4752 | 19.5524 | 16.139 | 13.2242 | 11.8351 | 13.2842 | 15.9448 | 19.9661 | 20.8473 | 22.5716 | 23.8707 | 18.3682
4555 | 22.8422 | 20.6496 | 19.6176 | 16.1513 | 13.1933 | 11.8795 | 13.4044 | 15.8798 | 19.9805 | 20.9142 | 22.5752 | 23.8345 | 18.4102
4556 | 24.2508 | 21.6552 | 20.3538 | 16.4221 | 13.2242 | 11.9199 | 13.4882 | 16.2944 | 20.7686 | 21.7387 | 23.4968 | 25.0454 | 19.0548
4557 | 24.9889 | 22.1036 | 20.9636 | 16.7655 | 13.2356 | 11.8192 | 13.4676 | 16.5063 | 21.0465 | 22.0237 | 24.0466 | 25.547 | 19.3762
4558 | 24.9599 | 22.1671 | 21.1791 | 16.8504 | 13.261 | 11.8554 | 13.5261 | 16.6352 | 21.0915 | 22.1329 | 24.4438 | 25.7597 | 19.4885
4559 | 23.5446 | 21.1674 | 20.0327 | 16.3868 | 13.3114 | 11.9024 | 13.475 | 16.1569 | 20.3878 | 21.4514 | 23.2261 | 24.5062 | 18.7957
4560 | 23.1445 | 20.9264 | 19.8257 | 16.3489 | 13.3252 | 11.9668 | 13.4719 | 15.9994 | 20.1285 | 21.0284 | 22.8294 | 24.0902 | 18.5904
4561 | 23.7632 | 21.4489 | 20.21 | 16.391 | 13.3313 | 12.0423 | 13.5816 | 16.3101 | 20.5885 | 21.467 | 23.3839 | 24.5427 | 18.9217
4562 | 23.4804 | 21.2566 | 20.0526 | 16.4008 | 13.4091 | 12.0953 | 13.514 | 16.1987 | 20.312 | 21.2066 | 23.182 | 24.2282 | 18.778
4563 | 23.4652 | 21.1616 | 20.0603 | 16.5961 | 13.5481 | 12.1193 | 13.5583 | 16.1044 | 20.1867 | 21.1886 | 23.0147 | 24.2372 | 18.77
4564 | 25.0109 | 22.3044 | 21.2431 | 16.906 | 13.3073 | 11.8583 | 13.5576 | 16.6281 | 21.1582 | 22.1597 | 24.6372 | 25.8787 | 19.5541
4565 | 24.0644 | 21.7972 | 20.6607 | 16.7833 | 13.5125 | 11.985 | 13.6737 | 16.6805 | 20.7783 | 21.8144 | 23.8735 | 25.1244 | 19.229
4566 | 24.7811 | 22.0763 | 21.0301 | 16.885 | 13.5819 | 12.0472 | 13.7669 | 16.666 | 21.1154 | 21.8623 | 24.1809 | 25.5177 | 19.4592
4567 | 25.3677 | 22.5052 | 21.4281 | 17.1348 | 13.6259 | 12.1171 | 13.875 | 16.8719 | 21.3098 | 22.4084 | 25.0126 | 26.2914 | 19.829
4568 | 23.1962 | 20.9055 | 19.7252 | 16.5914 | 13.5095 | 12.0763 | 13.5623 | 16.1448 | 20.0225 | 21.1428 | 22.9881 | 24.0404 | 18.6588
4569 | 23.5793 | 21.178 | 19.9641 | 16.6946 | 13.5424 | 12.0571 | 13.5515 | 16.1829 | 20.0893 | 21.337 | 23.2732 | 24.4035 | 18.8211
4570 | 23.7027 | 20.9669 | 20.026 | 16.8355 | 13.7096 | 12.3779 | 13.7225 | 16.2976 | 20.1337 | 21.3674 | 23.2151 | 24.627 | 18.9152
4571 | 23.5525 | 21.2053 | 19.9222 | 16.67 | 13.6111 | 12.1939 | 13.6732 | 16.3158 | 20.3605 | 21.414 | 23.2803 | 24.5051 | 18.892
4572 | 24.9599 | 22.1671 | 21.1791 | 16.8504 | 13.261 | 11.8554 | 13.5261 | 16.6352 | 21.0915 | 22.1329 | 24.4438 | 25.7597 | 19.4885
4573 | 25.0234 | 22.4238 | 21.2285 | 17.0242 | 13.3557 | 11.8978 | 13.607 | 16.6112 | 21.2415 | 22.2074 | 24.7193 | 25.9482 | 19.6073
4574 | 22.7351 | 20.3538 | 19.8515 | 16.1734 | 13.3073 | 11.9192 | 13.3349 | 15.9433 | 19.9129 | 20.8647 | 22.5782 | 23.9016 | 18.4063
4575 | 24.9145 | 22.255 | 20.8974 | 16.7463 | 13.2624 | 11.8571 | 13.4325 | 16.5431 | 21.0288 | 21.9909 | 23.9369 | 25.4023 | 19.3556
4580 | 23.7044 | 21.4931 | 20.3941 | 16.4553 | 13.7669 | 12.202 | 13.6398 | 16.4419 | 20.3979 | 21.321 | 23.4622 | 24.5608 | 18.9866
4581 | 24.6188 | 22.5345 | 20.7242 | 16.8867 | 13.8401 | 12.4982 | 13.8648 | 16.8617 | 20.3671 | 22.0027 | 24.1201 | 25.066 | 19.4487
4600 | 23.9074 | 21.3919 | 20.4287 | 16.8139 | 13.9323 | 12.2889 | 13.6175 | 16.5281 | 20.4872 | 21.7477 | 23.5001 | 25.151 | 19.1496
4601 | 24.4268 | 21.6737 | 20.833 | 17.2469 | 14.1327 | 12.5503 | 13.8675 | 16.6723 | 20.6916 | 21.94 | 23.7649 | 25.5871 | 19.4489
4605 | 24.5314 | 21.7916 | 20.5385 | 16.8625 | 14.0743 | 12.5804 | 13.7631 | 16.638 | 20.5416 | 22.1805 | 23.9872 | 25.5983 | 19.424
4606 | 24.2251 | 21.718 | 20.6509 | 17.0072 | 14.0832 | 12.3898 | 13.7857 | 16.709 | 20.5833 | 21.9335 | 23.9793 | 25.567 | 19.386
4608 | 24.2594 | 21.6106 | 20.6071 | 17.0515 | 14.124 | 12.3391 | 13.7101 | 16.6844 | 20.5892 | 21.9699 | 23.842 | 25.3257 | 19.3427
4610 | 24.5746 | 21.9083 | 21.1956 | 17.3295 | 14.1229 | 12.4234 | 13.7143 | 16.8456 | 20.6024 | 22.0276 | 24.0097 | 25.7161 | 19.5392
4611 | 24.5884 | 21.8663 | 20.7513 | 17.0044 | 14.182 | 12.5511 | 13.8583 | 16.7761 | 20.5955 | 22.0642 | 23.9674 | 25.5487 | 19.4795
4612 | 24.4646 | 21.8175 | 20.7201 | 16.873 | 14.1973 | 12.5119 | 13.8615 | 16.7876 | 20.6316 | 22.1542 | 24.0248 | 25.4834 | 19.4606
4613 | 24.706 | 21.9457 | 21.0143 | 17.1954 | 14.2253 | 12.677 | 13.9868 | 16.9725 | 20.8585 | 22.234 | 24.0779 | 25.5333 | 19.6189
4614 | 24.1782 | 20.9641 | 20.2973 | 16.7066 | 13.6512 | 12.0401 | 13.4482 | 16.446 | 20.3608 | 21.6892 | 23.3401 | 24.8455 | 18.9973
4615 | 24.2709 | 21.1979 | 20.5987 | 16.9143 | 13.7907 | 12.1505 | 13.524 | 16.5751 | 20.3271 | 21.5999 | 23.6112 | 25.1163 | 19.1397
4620 | 23.8419 | 21.3629 | 20.6255 | 17.2624 | 14.206 | 12.6978 | 14.0048 | 16.7445 | 20.5205 | 21.4036 | 23.2865 | 24.8164 | 19.2311
4621 | 23.886 | 21.6626 | 20.6727 | 17.2832 | 14.3385 | 12.7654 | 14.0725 | 16.9242 | 20.5282 | 21.645 | 23.5075 | 24.8836 | 19.3474
4625 | 24.8313 | 22.1309 | 21.1983 | 17.3398 | 14.4981 | 12.9833 | 14.1726 | 17.0728 | 20.9903 | 22.3405 | 24.6367 | 25.7514 | 19.8288
4626 | 25.1775 | 22.3819 | 21.3754 | 17.5321 | 14.6344 | 13.1108 | 14.3411 | 17.2684 | 21.2017 | 22.7801 | 24.834 | 26.1905 | 20.069
4627 | 24.737 | 21.9071 | 21.403 | 17.5983 | 14.6007 | 13.184 | 14.3326 | 17.2815 | 21.2639 | 22.5975 | 24.5264 | 25.8019 | 19.9362
4630 | 24.4036 | 21.5617 | 21.0156 | 17.4438 | 14.5715 | 13.1733 | 14.4184 | 17.1898 | 21.0331 | 22.352 | 24.024 | 25.1739 | 19.6967
4650 | 23.9592 | 21.7509 | 20.7653 | 17.022 | 14.0242 | 12.5386 | 13.8 | 16.6288 | 20.6033 | 21.5052 | 23.6013 | 24.9253 | 19.2603
4655 | 25.1037 | 22.782 | 21.1526 | 17.2717 | 14.3013 | 12.9246 | 14.374 | 17.3917 | 20.9559 | 22.1139 | 24.1662 | 25.669 | 19.8505
4659 | 24.3159 | 22.0659 | 20.7479 | 17.0813 | 14.379 | 12.9869 | 14.2234 | 17.0687 | 20.6984 | 21.7566 | 23.8097 | 25.021 | 19.5129
4660 | 24.0662 | 22.0129 | 20.897 | 17.1571 | 14.5219 | 12.9168 | 14.0752 | 17.0072 | 20.4842 | 21.6603 | 23.8025 | 24.8437 | 19.4537
4662 | 24.0271 | 21.924 | 20.7416 | 17.0103 | 14.2418 | 12.9605 | 14.0927 | 16.9109 | 20.5833 | 21.5621 | 23.5433 | 24.9081 | 19.3755
4670 | 24.8659 | 22.525 | 21.1999 | 17.6948 | 14.7901 | 13.2928 | 14.3501 | 17.4188 | 21.0904 | 22.3997 | 24.3516 | 25.3387 | 19.9431
4671 | 23.588 | 21.2914 | 20.4909 | 17.1541 | 14.4842 | 13.104 | 14.262 | 16.9789 | 20.6413 | 21.6665 | 23.6219 | 24.4918 | 19.3146
4673 | 25.2576 | 23.2065 | 21.7984 | 18.1893 | 14.8582 | 13.5521 | 14.8015 | 17.8816 | 21.9442 | 22.9538 | 24.854 | 25.8279 | 20.4271
4674 | 24.5077 | 22.7528 | 21.4426 | 18.0061 | 14.8948 | 13.5143 | 14.6191 | 17.6879 | 21.5635 | 22.7484 | 24.4273 | 25.1958 | 20.1134
4676 | 23.3178 | 21.4534 | 20.6296 | 17.4023 | 14.5916 | 13.1698 | 14.2935 | 17.083 | 20.6824 | 21.879 | 23.3878 | 24.1117 | 19.3335
4677 | 23.8509 | 21.8699 | 20.964 | 17.5821 | 14.7323 | 13.2873 | 14.5147 | 17.1995 | 20.8455 | 22.1697 | 23.687 | 24.5063 | 19.6008
4678 | 24.3278 | 22.263 | 21.2715 | 17.9509 | 14.9516 | 13.5259 | 14.8281 | 17.517 | 21.1613 | 22.3993 | 24.1509 | 25.0028 | 19.9458
4680 | 24.0344 | 21.8892 | 21.1898 | 17.7772 | 15.1082 | 13.5696 | 14.836 | 17.1607 | 20.9045 | 22.0543 | 23.6869 | 24.3271 | 19.7115
4694 | 25.512 | 23.1838 | 22.4853 | 18.6011 | 15.657 | 14.06 | 15.4306 | 18.107 | 21.7563 | 23.277 | 25.4523 | 25.6644 | 20.7656
4695 | 24.4862 | 22.4905 | 21.6167 | 18.0844 | 15.3174 | 13.9188 | 15.1926 | 17.558 | 21.3628 | 22.8417 | 24.781 | 25.1138 | 20.2303
4699 | 24.6024 | 22.2945 | 21.6708 | 18.0208 | 15.4901 | 13.9329 | 15.2716 | 17.6457 | 21.7158 | 23.073 | 25.013 | 25.219 | 20.3291
4700 | 25.1009 | 22.5903 | 22.0517 | 18.2082 | 15.7737 | 13.9618 | 15.3461 | 17.6855 | 21.7901 | 23.1529 | 25.0764 | 25.2545 | 20.4993
4701 | 24.8314 | 22.3298 | 21.8106 | 18.1061 | 15.5829 | 13.8719 | 15.254 | 17.6913 | 21.81 | 23.1831 | 25.0087 | 25.1194 | 20.3833
4702 | 24.3774 | 21.9275 | 21.7567 | 17.7035 | 15.7252 | 13.9081 | 15.3996 | 17.6537 | 21.7994 | 23.0963 | 24.8311 | 25.3319 | 20.2925
4703 | 23.5334 | 21.4563 | 20.9093 | 17.3984 | 15.133 | 13.6306 | 15.0945 | 17.3736 | 21.6018 | 22.9282 | 24.3238 | 24.5905 | 19.8311
4705 | 24.7184 | 22.1093 | 22.5795 | 18.572 | 16.2528 | 14.3742 | 15.9666 | 18.4633 | 22.3903 | 23.667 | 25.1591 | 25.7001 | 20.8294
4707 | 24.6908 | 22.2755 | 22.0453 | 18.0935 | 16.133 | 14.4895 | 15.9043 | 18.5602 | 22.8915 | 24.2544 | 25.518 | 25.7438 | 20.8833
4709 | 24.9687 | 22.4005 | 22.7832 | 18.8981 | 16.2669 | 14.2964 | 15.9037 | 18.3916 | 22.4627 | 23.6519 | 25.1239 | 25.6293 | 20.8981
4710 | 25.4496 | 23.3334 | 22.7495 | 18.4373 | 15.8194 | 13.9225 | 15.4628 | 18.2921 | 22.6479 | 23.836 | 25.8077 | 25.6503 | 20.9507
4711 | 24.8751 | 22.2926 | 21.8378 | 18.0892 | 15.7217 | 13.9096 | 15.2613 | 17.7192 | 21.7268 | 23.2601 | 25.0343 | 25.2847 | 20.4177
4712 | 24.9887 | 22.2044 | 22.1159 | 18.0985 | 15.8048 | 14.051 | 15.491 | 17.809 | 21.8225 | 23.1929 | 25.0557 | 25.4731 | 20.509
4713 | 25.3998 | 22.4175 | 22.2991 | 18.5822 | 15.6931 | 14.0157 | 15.3769 | 18.0298 | 21.8848 | 23.0452 | 24.9808 | 25.8012 | 20.6272
4714 | 24.4443 | 22.033 | 21.6385 | 17.8093 | 15.348 | 13.6563 | 15.0592 | 17.4561 | 21.5032 | 22.9645 | 24.7078 | 25.1559 | 20.148
4715 | 25.4302 | 22.4553 | 21.9593 | 18.2494 | 15.3149 | 13.7141 | 15.028 | 17.7523 | 21.6668 | 23.0664 | 24.9374 | 25.9991 | 20.4644
4716 | 25.0059 | 22.4615 | 21.7961 | 17.9363 | 15.2262 | 13.6799 | 14.9232 | 17.7244 | 21.7034 | 22.8831 | 24.7834 | 25.6066 | 20.3108
4717 | 25.7347 | 23.1451 | 22.6714 | 18.8726 | 16.1859 | 14.4884 | 15.8462 | 18.4586 | 22.2833 | 23.703 | 25.5417 | 26.4188 | 21.1125
4718 | 26.069 | 22.8818 | 22.4817 | 18.599 | 15.6981 | 14.0576 | 15.3444 | 18.116 | 21.9579 | 23.2919 | 25.3298 | 26.1967 | 20.8353
4719 | 26.042 | 22.9939 | 22.1491 | 18.3088 | 15.3114 | 13.6488 | 14.9577 | 17.8106 | 21.8811 | 23.1702 | 25.2056 | 26.4008 | 20.6567
4720 | 25.5101 | 23.2223 | 23.2139 | 19.0798 | 16.3 | 14.3625 | 15.8696 | 18.2963 | 22.2493 | 23.5789 | 25.494 | 26.0998 | 21.1064
4721 | 25.628 | 23.4945 | 23.2724 | 19.3646 | 16.7401 | 14.9328 | 16.5589 | 19.1758 | 23.1912 | 24.4006 | 25.8787 | 26.4638 | 21.5918
4722 | 25.4777 | 23.3003 | 23.1069 | 19.0777 | 15.9813 | 14.2009 | 15.4551 | 18.2935 | 22.2593 | 23.5394 | 25.2778 | 26.3044 | 21.0229
4723 | 25.2119 | 22.5736 | 22.896 | 18.8574 | 16.1585 | 14.457 | 16.0266 | 18.5159 | 22.7072 | 23.7773 | 25.4613 | 25.787 | 21.0358
4724 | 26.0345 | 23.8598 | 23.1118 | 19.3872 | 16.3886 | 14.7202 | 15.7975 | 18.5794 | 22.4063 | 23.9959 | 25.6101 | 26.6574 | 21.3791
4725 | 26.4398 | 25.0074 | 23.629 | 19.7465 | 16.5809 | 15.0567 | 16.3011 | 19.2589 | 23.0944 | 24.5775 | 26.1601 | 27.3719 | 21.9353
4726 | 26.3629 | 25.1443 | 23.9183 | 20.4519 | 17.1129 | 15.6773 | 16.9238 | 19.7167 | 23.4717 | 25.0732 | 26.6513 | 27.1716 | 22.3063
4727 | 26.6629 | 25.352 | 23.6385 | 19.6084 | 16.4339 | 14.844 | 16.0893 | 19.2713 | 22.9214 | 24.6004 | 26.2547 | 27.2442 | 21.9101
4728 | 26.2387 | 24.2594 | 23.4364 | 19.6112 | 16.4636 | 14.855 | 16.0765 | 18.9126 | 22.8326 | 24.1672 | 26.0285 | 26.9156 | 21.6498
4730 | 26.6448 | 25.5418 | 24.1125 | 20.3132 | 16.8344 | 15.165 | 16.6254 | 19.5747 | 23.0723 | 24.6738 | 26.1442 | 27.3089 | 22.1676
4731 | 26.9651 | 25.505 | 23.7762 | 19.626 | 16.3735 | 14.5375 | 15.923 | 19.2333 | 22.7273 | 24.5603 | 26.0772 | 27.3496 | 21.8878
4733 | 26.2484 | 25.4644 | 24.0953 | 20.6385 | 17.2594 | 15.5942 | 17.0007 | 19.9553 | 23.3461 | 24.8202 | 26.3342 | 26.9864 | 22.3119
4735 | 26.2546 | 25.4194 | 24.025 | 20.4471 | 17.2493 | 15.6066 | 17.1036 | 19.9582 | 23.3398 | 25.1819 | 26.572 | 27.1112 | 22.3557
4737 | 23.0758 | 20.4082 | 21.1063 | 17.7813 | 15.7359 | 14.288 | 15.6119 | 17.7812 | 22.2636 | 23.0008 | 23.7147 | 24.1524 | 19.91
4738 | 24.1812 | 21.2568 | 21.8862 | 18.3866 | 16.2323 | 14.61 | 15.8738 | 18.1592 | 22.5644 | 23.4723 | 24.1368 | 24.9561 | 20.4763
4739 | 23.9233 | 21.2706 | 21.7689 | 18.0352 | 16.0214 | 14.5462 | 15.8226 | 18.0937 | 22.5326 | 23.1638 | 23.7462 | 24.7658 | 20.3075
4740 | 24.2322 | 21.4205 | 21.8447 | 18.4297 | 16.1604 | 14.6791 | 15.9414 | 18.4069 | 22.7574 | 23.8136 | 24.5624 | 25.0682 | 20.6097
4741 | 22.8148 | 19.6399 | 20.8553 | 17.5505 | 15.6805 | 14.1597 | 15.2482 | 17.5975 | 22.0732 | 22.967 | 23.4944 | 23.7359 | 19.6514
4742 | 24.2121 | 21.8272 | 21.9457 | 18.3809 | 16.0649 | 14.4885 | 15.9127 | 18.2157 | 22.6237 | 23.9199 | 24.9955 | 25.2911 | 20.6565
4743 | 24.4346 | 22.042 | 22.1952 | 18.9307 | 16.553 | 14.7793 | 16.3048 | 18.737 | 22.8201 | 24.14 | 25.1056 | 25.2763 | 20.9432
4744 | 25.3352 | 22.7251 | 22.7899 | 19.0864 | 16.6235 | 14.921 | 16.5864 | 18.9079 | 23.0113 | 24.3912 | 25.69 | 25.9121 | 21.3317
4745 | 24.6173 | 21.8528 | 22.3007 | 18.5076 | 16.1393 | 14.4082 | 15.9671 | 18.4214 | 22.6558 | 23.712 | 25.0014 | 25.3027 | 20.7405
4746 | 24.6235 | 22.1113 | 22.2768 | 18.4427 | 16.2629 | 14.4048 | 16.0331 | 18.4918 | 22.4515 | 23.5668 | 25.2335 | 25.6279 | 20.7939
4750 | 24.8423 | 21.8659 | 21.8975 | 18.6019 | 16.0632 | 14.8198 | 16.382 | 19.1821 | 23.54 | 24.3342 | 25.3072 | 25.5384 | 21.0312
4751 | 24.1478 | 21.1989 | 21.6084 | 18.1793 | 16.0635 | 14.5284 | 15.9076 | 18.3259 | 22.5472 | 23.6605 | 24.5697 | 25.0052 | 20.4785
4753 | 23.5245 | 20.584 | 21.2458 | 17.7283 | 15.7271 | 14.294 | 15.4874 | 17.9656 | 22.3277 | 23.2661 | 24.1164 | 24.4357 | 20.0586
4754 | 23.0806 | 20.1404 | 21.0596 | 17.6082 | 15.6287 | 14.0566 | 15.2327 | 17.7266 | 22.1142 | 23.1775 | 23.7428 | 24.2261 | 19.8162
4756 | 21.107 | 18.5246 | 19.4182 | 15.8695 | 14.9046 | 13.0432 | 14.6349 | 16.9674 | 21.2399 | 22.168 | 22.3456 | 22.4534 | 18.5564
4757 | 22.4132 | 19.6721 | 20.5598 | 17.4604 | 15.6458 | 14.0583 | 15.4456 | 17.7356 | 22.1295 | 23.1835 | 23.8451 | 23.8241 | 19.6644
4798 | 24.1488 | 21.0834 | 21.4978 | 18.5858 | 16.0762 | 14.8662 | 16.2918 | 18.9048 | 23.4794 | 24.2545 | 25.022 | 24.8913 | 20.7585
4799 | 23.7403 | 21.0097 | 21.6067 | 18.6814 | 16.3058 | 14.9665 | 16.2422 | 18.6994 | 23.2591 | 24.3088 | 24.8905 | 24.8167 | 20.7106
4800 | 23.7183 | 20.7723 | 21.0444 | 18.07 | 16.0192 | 14.5417 | 16.0858 | 18.5271 | 22.4705 | 23.7917 | 24.5863 | 24.449 | 20.3397
4801 | 25.9868 | 23.2144 | 22.4251 | 19.403 | 16.4792 | 15.2346 | 16.8173 | 19.7701 | 24.1415 | 25.8688 | 26.7946 | 26.5181 | 21.8878
4802 | 24.5166 | 21.1497 | 21.1223 | 18.7419 | 16.056 | 14.9821 | 16.6836 | 19.12 | 23.4817 | 24.6397 | 25.2518 | 25.0249 | 20.8975
4803 | 24.072 | 21.6632 | 20.518 | 17.2493 | 15.1995 | 14.1105 | 15.6067 | 18.3278 | 22.4453 | 23.7943 | 24.5109 | 24.5407 | 20.1699
4804 | 24.3936 | 22.0272 | 22.3106 | 19.179 | 16.7584 | 15.129 | 16.8001 | 19.0944 | 23.0353 | 24.4938 | 24.9333 | 25.2968 | 21.121
4805 | 24.4717 | 21.7817 | 21.6131 | 19.2467 | 16.8247 | 15.4992 | 17.0396 | 19.145 | 22.9649 | 24.5412 | 25.3006 | 25.2738 | 21.1419
4806 | 24.2819 | 21.8576 | 21.7608 | 19.1926 | 16.8332 | 15.5922 | 17.1283 | 19.3291 | 23.4193 | 24.7013 | 25.3395 | 25.0851 | 21.2101
4807 | 24.0205 | 21.9024 | 22.0091 | 18.8833 | 16.766 | 15.2943 | 16.762 | 19.0204 | 22.8617 | 24.2635 | 24.4707 | 24.7565 | 20.9175
4808 | 25.9608 | 22.5678 | 22.7555 | 20.2704 | 17.1922 | 15.8999 | 17.3823 | 19.9885 | 23.7174 | 24.9354 | 25.716 | 25.924 | 21.8592
4809 | 24.2882 | 21.5646 | 21.8492 | 19.2095 | 16.8438 | 15.4743 | 16.7465 | 19.1967 | 22.9421 | 24.1083 | 24.7075 | 24.9714 | 20.9918
4810 | 25.2893 | 22.082 | 22.4773 | 19.9687 | 17.2426 | 15.8599 | 17.4256 | 19.9802 | 23.6521 | 24.8132 | 25.3415 | 25.5446 | 21.6397
4811 | 24.6295 | 21.4594 | 21.6727 | 19.2876 | 16.8076 | 15.5335 | 17.0538 | 19.4303 | 23.2271 | 24.6682 | 25.1559 | 24.9478 | 21.1561
4812 | 24.9498 | 21.5276 | 21.9158 | 19.5073 | 16.7986 | 15.6667 | 17.169 | 19.5595 | 23.4803 | 24.6657 | 25.0577 | 25.2428 | 21.2951
4813 | 24.6295 | 21.4594 | 21.6727 | 19.2876 | 16.8076 | 15.5335 | 17.0538 | 19.4303 | 23.2271 | 24.6682 | 25.1559 | 24.9478 | 21.1561
4814 | 25.0131 | 21.66 | 21.8617 | 19.3679 | 16.8256 | 15.6742 | 17.1815 | 19.5943 | 23.3558 | 24.6947 | 25.2041 | 25.3776 | 21.3175
4815 | 23.6237 | 20.7951 | 21.6452 | 18.7899 | 16.6175 | 15.3597 | 16.572 | 18.7243 | 22.6141 | 23.9833 | 24.1481 | 24.056 | 20.5774
4816 | 25.4119 | 24.3744 | 23.9183 | 20.869 | 17.6842 | 16.1498 | 17.5869 | 20.2258 | 23.8645 | 25.3368 | 26.4859 | 26.3244 | 22.3527
4817 | 23.8859 | 21.316 | 21.9957 | 19.1102 | 16.6543 | 15.1933 | 16.5025 | 18.8274 | 23.3719 | 24.7262 | 25.0631 | 24.6546 | 20.9418
4818 | 24.5813 | 21.3836 | 21.6813 | 19.0552 | 16.8921 | 15.5741 | 16.9718 | 19.3743 | 23.1195 | 24.5136 | 24.8192 | 25.0027 | 21.0807
4819 | 25.4778 | 22.2097 | 22.8361 | 20.2872 | 17.509 | 16.0284 | 17.5333 | 20.1849 | 24.3098 | 25.654 | 26.035 | 25.9465 | 22.001
4820 | 24.8546 | 22.3944 | 22.7321 | 19.9464 | 17.2806 | 15.6722 | 17.1181 | 19.584 | 23.4832 | 24.5668 | 25.0657 | 25.1804 | 21.4899
4821 | 25.5348 | 24.537 | 23.8271 | 20.9942 | 17.8261 | 16.4705 | 17.6829 | 20.5423 | 23.9393 | 25.4682 | 26.5048 | 26.6907 | 22.5015
4822 | 25.686 | 24.9108 | 24.2713 | 21.4536 | 18.137 | 16.8035 | 17.9079 | 20.7229 | 24.0803 | 25.8025 | 26.7371 | 26.4008 | 22.7428
4823 | 25.5745 | 25.0408 | 23.7719 | 21.1369 | 18.0775 | 16.8917 | 17.9798 | 20.942 | 23.9865 | 25.6415 | 26.5025 | 26.2031 | 22.6457
4824 | 25.3299 | 24.452 | 24.3072 | 21.7964 | 18.5615 | 17.274 | 18.5096 | 21.2141 | 23.9486 | 25.8043 | 26.4753 | 25.704 | 22.7814
4825 | 25.2868 | 24.2298 | 23.7019 | 21.2476 | 18.0249 | 16.5441 | 17.9349 | 20.8369 | 23.716 | 25.1225 | 25.7408 | 25.8899 | 22.3563
4828 | 25.9798 | 24.3824 | 23.7867 | 21.4916 | 18.5419 | 17.2775 | 18.3787 | 21.3331 | 24.148 | 25.4941 | 26.1037 | 26.2075 | 22.7604
4829 | 27.6918 | 25.8007 | 23.6585 | 19.9404 | 16.6759 | 14.7699 | 15.9815 | 19.2509 | 22.5496 | 25.0043 | 27.1103 | 27.4679 | 22.1585
4830 | 22.5427 | 21.2814 | 23.1096 | 21.8914 | 19.3665 | 18.0268 | 19.3847 | 21.9805 | 24.2906 | 25.3902 | 25.2699 | 23.7004 | 22.1862
4849 | 21.1796 | 18.6298 | 18.8286 | 16.4635 | 15.1378 | 13.8172 | 15.0131 | 16.7072 | 21.5232 | 22.4532 | 22.175 | 22.2986 | 18.6856
4850 | 23.0994 | 20.0161 | 20.5068 | 17.6981 | 16.0334 | 14.2478 | 15.3579 | 17.4594 | 21.5732 | 23.4951 | 23.9487 | 23.9862 | 19.7852
4852 | 22.7032 | 20.0527 | 19.6416 | 16.6848 | 15.1045 | 13.5564 | 15.2528 | 17.6261 | 22.5996 | 24.3545 | 23.9114 | 23.7867 | 19.6062
4854 | 21.8118 | 18.565 | 18.6756 | 16.0664 | 14.7308 | 13.0472 | 14.3619 | 16.6538 | 21.5418 | 23.2128 | 23.1774 | 22.9497 | 18.7328
4855 | 22.7147 | 20.0162 | 19.3631 | 16.9926 | 15.3242 | 13.8206 | 15.4523 | 17.7455 | 22.7694 | 24.4145 | 23.8273 | 23.8294 | 19.6892
4856 | 20.6139 | 17.542 | 17.5942 | 15.654 | 14.4681 | 12.8265 | 14.0684 | 16.2591 | 20.919 | 22.2423 | 22.1274 | 21.7492 | 18.0053
4857 | 19.3311 | 16.991 | 18.7328 | 20.1832 | 19.32 | 18.8555 | 20.0863 | 22.5332 | 24.4761 | 25.108 | 24.0362 | 21.3289 | 20.9152
4858 | 22.7991 | 20.0327 | 18.9952 | 17.2278 | 15.163 | 13.642 | 15.1377 | 17.821 | 22.8268 | 24.4585 | 23.7605 | 23.7632 | 19.6356
4859 | 22.4981 | 19.5675 | 18.4946 | 16.7575 | 15.1284 | 13.4954 | 14.8748 | 17.2974 | 22.0805 | 23.9348 | 23.3906 | 23.5203 | 19.2533
4860 | 21.3277 | 18.2859 | 17.1788 | 16.3006 | 15.369 | 14.231 | 15.4475 | 17.1076 | 21.3679 | 22.8263 | 21.8193 | 21.6829 | 18.5787
4861 | 21.1512 | 18.4648 | 17.104 | 15.5665 | 14.3431 | 12.9678 | 14.0445 | 16.1124 | 21.1837 | 22.5194 | 21.7899 | 21.7664 | 18.0845
4865 | 22.2586 | 19.1294 | 18.6006 | 17.798 | 16.0953 | 14.6018 | 15.7976 | 17.8251 | 22.2968 | 23.7321 | 23.2952 | 22.9243 | 19.5296
4868 | 22.8766 | 19.8016 | 19.1473 | 18.4072 | 16.7705 | 15.2515 | 16.7101 | 18.9525 | 22.8615 | 24.0967 | 23.4583 | 23.1925 | 20.1272
4869 | 22.4447 | 19.4115 | 18.7528 | 17.9435 | 16.3419 | 14.7316 | 16.1107 | 18.265 | 22.3483 | 23.7963 | 23.1429 | 22.9542 | 19.6869
4870 | 21.8038 | 18.9955 | 18.4529 | 17.5763 | 16.2713 | 14.6779 | 15.9766 | 17.9572 | 21.9725 | 23.1957 | 22.7423 | 22.345 | 19.3306
4871 | 23.191 | 21.8223 | 22.3711 | 22.0385 | 19.1289 | 17.9372 | 19.1973 | 21.3104 | 24.4146 | 25.5571 | 26.3136 | 24.5275 | 22.3175
4872 | 22.65 | 20.2867 | 20.2912 | 18.2876 | 15.9504 | 14.4805 | 15.9935 | 18.378 | 22.9314 | 24.1869 | 24.3251 | 23.371 | 20.0944
4873 | 21.6727 | 18.8081 | 18.7156 | 18.0321 | 16.077 | 14.917 | 16.2423 | 18.5301 | 22 | 23.8195 | 23.8474 | 22.7003 | 19.6135
4874 | 18.1625 | 15.9357 | 18.0564 | 20.0408 | 18.2942 | 16.922 | 17.9248 | 20.4335 | 22.7491 | 23.8899 | 23.0995 | 20.6095 | 19.6765
4875 | 18.9507 | 16.4078 | 18.4447 | 20.0332 | 19.1799 | 18.5411 | 19.7933 | 22.1475 | 23.92 | 24.5838 | 23.6773 | 20.9259 | 20.5504
4876 | 18.4776 | 16.2267 | 17.574 | 19.7079 | 18.5523 | 17.6753 | 18.9014 | 21.3102 | 22.6547 | 23.6071 | 23.2574 | 20.5193 | 19.872
4877 | 23.0961 | 20.2406 | 19.8341 | 19.4803 | 17.2532 | 15.665 | 17.1482 | 19.8368 | 23.8124 | 24.8353 | 24.1833 | 23.6377 | 20.7519
4878 | 23.2962 | 20.3024 | 19.4655 | 18.8307 | 17.0279 | 15.6443 | 17.1813 | 19.4995 | 23.2902 | 24.5125 | 23.6319 | 23.2789 | 20.4968
4879 | 23.6775 | 20.597 | 19.9907 | 19.3968 | 17.3823 | 15.9795 | 17.5864 | 20.0278 | 23.8066 | 25.253 | 24.5715 | 23.7952 | 21.0054
4880 | 22.3589 | 19.8803 | 19.7318 | 19.3316 | 16.7855 | 15.5068 | 16.9766 | 19.1133 | 23.2652 | 24.7055 | 24.6213 | 23.476 | 20.4794
4881 | 22.3566 | 19.7403 | 19.2998 | 18.6202 | 16.7771 | 15.2896 | 16.6423 | 18.8449 | 22.2941 | 24.002 | 24.0034 | 23.2603 | 20.0942
4882 | 21.9167 | 19.1033 | 19.3163 | 18.9639 | 16.7449 | 15.4692 | 17.0047 | 18.7283 | 23.2212 | 24.3852 | 24.145 | 22.6385 | 20.1364
4883 | 21.0674 | 18.4307 | 18.3438 | 17.2468 | 15.4454 | 14.1694 | 15.7246 | 17.7011 | 22.2339 | 23.6122 | 23.3187 | 22.0003 | 19.1079
4884 | 21.3501 | 18.2885 | 18.2881 | 16.9199 | 15.2187 | 13.8651 | 15.2567 | 17.4878 | 22.3541 | 23.5239 | 23.3125 | 22.2883 | 19.0128
4885 | 21.1672 | 18.1718 | 17.7549 | 16.4409 | 14.8017 | 13.4834 | 14.913 | 16.9669 | 21.9541 | 23.2454 | 23.2079 | 22.2435 | 18.6959
4886 | 20.2337 | 17.7295 | 17.0424 | 15.6313 | 14.3859 | 12.9546 | 14.4172 | 16.667 | 21.2707 | 22.803 | 22.394 | 21.4974 | 18.0856
4887 | 21.6845 | 19.8658 | 20.0288 | 19.1944 | 17.0271 | 15.7924 | 17.4347 | 19.4751 | 23.5232 | 24.4995 | 24.4566 | 22.8875 | 20.4891
4888 | 21.0272 | 18.6729 | 18.4157 | 17.2559 | 15.3108 | 14.1519 | 15.802 | 18.0721 | 22.1362 | 23.7653 | 23.5408 | 22.2844 | 19.2029
4890 | 21.8746 | 20.5769 | 22.32 | 22.4733 | 19.3152 | 18.0999 | 19.3301 | 21.5788 | 24.577 | 25.7374 | 25.3332 | 22.9836 | 22.0167
4891 | 22.7565 | 21.0409 | 22.6975 | 22.1459 | 19.1011 | 18.0081 | 19.3582 | 21.7169 | 23.3857 | 24.8284 | 25.278 | 23.4725 | 21.9825
4895 | 21.6227 | 19.7434 | 19.6055 | 19.4586 | 17.5256 | 16.2091 | 17.1027 | 19.6568 | 22.5509 | 24.0316 | 24.2005 | 23.3493 | 20.4214
5000 | 27.7668 | 24.2785 | 19.9084 | 13.6936 | 9.3212 | 7.3771 | 8.4656 | 11.9131 | 15.1945 | 20.0337 | 24.6671 | 27.3033 | 17.4936
5005 | 27.8781 | 24.4361 | 20.0797 | 13.7954 | 9.4484 | 7.4541 | 8.5734 | 12.0564 | 15.3081 | 20.2124 | 24.7727 | 27.3882 | 17.6169
5006 | 27.8781 | 24.4361 | 20.0797 | 13.7954 | 9.4484 | 7.4541 | 8.5734 | 12.0564 | 15.3081 | 20.2124 | 24.7727 | 27.3882 | 17.6169
5007 | 28.0282 | 24.4883 | 19.9906 | 13.8702 | 9.7074 | 7.6508 | 8.7624 | 12.1827 | 15.4727 | 20.519 | 24.9034 | 27.4914 | 17.7556
5008 | 28.0282 | 24.4883 | 19.9906 | 13.8702 | 9.7074 | 7.6508 | 8.7624 | 12.1827 | 15.4727 | 20.519 | 24.9034 | 27.4914 | 17.7556
5009 | 28.0282 | 24.4883 | 19.9906 | 13.8702 | 9.7074 | 7.6508 | 8.7624 | 12.1827 | 15.4727 | 20.519 | 24.9034 | 27.4914 | 17.7556
5010 | 27.7329 | 24.1798 | 20.0059 | 13.8848 | 9.7783 | 7.6944 | 8.7977 | 12.2185 | 15.6187 | 20.57 | 24.959 | 27.2186 | 17.7216
5011 | 28.0282 | 24.4883 | 19.9906 | 13.8702 | 9.7074 | 7.6508 | 8.7624 | 12.1827 | 15.4727 | 20.519 | 24.9034 | 27.4914 | 17.7556
5012 | 27.7329 | 24.1798 | 20.0059 | 13.8848 | 9.7783 | 7.6944 | 8.7977 | 12.2185 | 15.6187 | 20.57 | 24.959 | 27.2186 | 17.7216
5013 | 27.7329 | 24.1798 | 20.0059 | 13.8848 | 9.7783 | 7.6944 | 8.7977 | 12.2185 | 15.6187 | 20.57 | 24.959 | 27.2186 | 17.7216
5014 | 27.9452 | 24.356 | 20.0999 | 14.0157 | 9.8433 | 7.7631 | 8.9446 | 12.3942 | 15.7405 | 20.6899 | 25.043 | 27.4586 | 17.8578
5015 | 27.9452 | 24.356 | 20.0999 | 14.0157 | 9.8433 | 7.7631 | 8.9446 | 12.3942 | 15.7405 | 20.6899 | 25.043 | 27.4586 | 17.8578
5016 | 27.7473 | 24.0122 | 20.1284 | 14.0472 | 9.8218 | 7.7459 | 8.945 | 12.3538 | 15.9015 | 20.8045 | 25.1003 | 27.363 | 17.8309
5017 | 27.7473 | 24.0122 | 20.1284 | 14.0472 | 9.8218 | 7.7459 | 8.945 | 12.3538 | 15.9015 | 20.8045 | 25.1003 | 27.363 | 17.8309
5018 | 27.7473 | 24.0122 | 20.1284 | 14.0472 | 9.8218 | 7.7459 | 8.945 | 12.3538 | 15.9015 | 20.8045 | 25.1003 | 27.363 | 17.8309
5019 | 27.9452 | 24.356 | 20.0999 | 14.0157 | 9.8433 | 7.7631 | 8.9446 | 12.3942 | 15.7405 | 20.6899 | 25.043 | 27.4586 | 17.8578
5020 | 27.9452 | 24.356 | 20.0999 | 14.0157 | 9.8433 | 7.7631 | 8.9446 | 12.3942 | 15.7405 | 20.6899 | 25.043 | 27.4586 | 17.8578
5021 | 27.9452 | 24.356 | 20.0999 | 14.0157 | 9.8433 | 7.7631 | 8.9446 | 12.3942 | 15.7405 | 20.6899 | 25.043 | 27.4586 | 17.8578
5022 | 27.9846 | 24.4323 | 20.0881 | 13.8633 | 9.698 | 7.6985 | 8.934 | 12.3907 | 15.7356 | 20.7494 | 25.1071 | 27.5125 | 17.8495
5023 | 27.9846 | 24.4323 | 20.0881 | 13.8633 | 9.698 | 7.6985 | 8.934 | 12.3907 | 15.7356 | 20.7494 | 25.1071 | 27.5125 | 17.8495
5024 | 27.9007 | 24.2765 | 20.022 | 13.7852 | 9.4974 | 7.6466 | 8.8812 | 12.342 | 15.7819 | 20.7351 | 25.2243 | 27.6059 | 17.8082
5025 | 28.0282 | 24.4883 | 19.9906 | 13.8702 | 9.7074 | 7.6508 | 8.7624 | 12.1827 | 15.4727 | 20.519 | 24.9034 | 27.4914 | 17.7556
5031 | 28.0129 | 24.5288 | 19.9915 | 13.8265 | 9.5051 | 7.5604 | 8.7333 | 12.2301 | 15.5101 | 20.4485 | 25.0066 | 27.5475 | 17.7418
5032 | 28.0282 | 24.4883 | 19.9906 | 13.8702 | 9.7074 | 7.6508 | 8.7624 | 12.1827 | 15.4727 | 20.519 | 24.9034 | 27.4914 | 17.7556
5033 | 28.0129 | 24.5288 | 19.9915 | 13.8265 | 9.5051 | 7.5604 | 8.7333 | 12.2301 | 15.5101 | 20.4485 | 25.0066 | 27.5475 | 17.7418
5034 | 27.7668 | 24.2785 | 19.9084 | 13.6936 | 9.3212 | 7.3771 | 8.4656 | 11.9131 | 15.1945 | 20.0337 | 24.6671 | 27.3033 | 17.4936
5035 | 27.7668 | 24.2785 | 19.9084 | 13.6936 | 9.3212 | 7.3771 | 8.4656 | 11.9131 | 15.1945 | 20.0337 | 24.6671 | 27.3033 | 17.4936
5037 | 28.0129 | 24.5288 | 19.9915 | 13.8265 | 9.5051 | 7.5604 | 8.7333 | 12.2301 | 15.5101 | 20.4485 | 25.0066 | 27.5475 | 17.7418
5038 | 28.0129 | 24.5288 | 19.9915 | 13.8265 | 9.5051 | 7.5604 | 8.7333 | 12.2301 | 15.5101 | 20.4485 | 25.0066 | 27.5475 | 17.7418
5039 | 27.8941 | 24.3975 | 19.8665 | 13.76 | 9.3413 | 7.5146 | 8.5768 | 12.0949 | 15.5202 | 20.2507 | 24.9301 | 27.4975 | 17.637
5040 | 28.0129 | 24.5288 | 19.9915 | 13.8265 | 9.5051 | 7.5604 | 8.7333 | 12.2301 | 15.5101 | 20.4485 | 25.0066 | 27.5475 | 17.7418
5041 | 27.5454 | 24.2201 | 19.7099 | 13.6734 | 9.1355 | 7.2446 | 8.3184 | 11.7475 | 15.1592 | 19.7842 | 24.5762 | 27.2257 | 17.3617
5042 | 27.5454 | 24.2201 | 19.7099 | 13.6734 | 9.1355 | 7.2446 | 8.3184 | 11.7475 | 15.1592 | 19.7842 | 24.5762 | 27.2257 | 17.3617
5043 | 27.8941 | 24.3975 | 19.8665 | 13.76 | 9.3413 | 7.5146 | 8.5768 | 12.0949 | 15.5202 | 20.2507 | 24.9301 | 27.4975 | 17.637
5044 | 27.8941 | 24.3975 | 19.8665 | 13.76 | 9.3413 | 7.5146 | 8.5768 | 12.0949 | 15.5202 | 20.2507 | 24.9301 | 27.4975 | 17.637
5045 | 27.5982 | 24.1028 | 19.9622 | 13.6937 | 9.3837 | 7.5826 | 8.7912 | 12.2049 | 15.6941 | 20.5715 | 25.1555 | 27.3016 | 17.6702
5046 | 27.8941 | 24.3975 | 19.8665 | 13.76 | 9.3413 | 7.5146 | 8.5768 | 12.0949 | 15.5202 | 20.2507 | 24.9301 | 27.4975 | 17.637
5047 | 27.66 | 24.2947 | 19.7044 | 13.7437 | 9.2293 | 7.3483 | 8.4486 | 11.9529 | 15.3864 | 20.066 | 24.7761 | 27.3493 | 17.4966
5048 | 27.8941 | 24.3975 | 19.8665 | 13.76 | 9.3413 | 7.5146 | 8.5768 | 12.0949 | 15.5202 | 20.2507 | 24.9301 | 27.4975 | 17.637
5049 | 27.66 | 24.2947 | 19.7044 | 13.7437 | 9.2293 | 7.3483 | 8.4486 | 11.9529 | 15.3864 | 20.066 | 24.7761 | 27.3493 | 17.4966
5050 | 27.5454 | 24.2201 | 19.7099 | 13.6734 | 9.1355 | 7.2446 | 8.3184 | 11.7475 | 15.1592 | 19.7842 | 24.5762 | 27.2257 | 17.3617
5051 | 27.3278 | 24.0759 | 19.598 | 13.6071 | 8.9452 | 7.0633 | 8.1949 | 11.5776 | 15.0184 | 19.5829 | 24.3982 | 27.0396 | 17.2024
5052 | 27.3208 | 23.9884 | 19.6262 | 13.5422 | 8.8361 | 6.8557 | 8.072 | 11.374 | 14.7308 | 19.2602 | 24.1701 | 26.9345 | 17.0592
5061 | 27.7668 | 24.2785 | 19.9084 | 13.6936 | 9.3212 | 7.3771 | 8.4656 | 11.9131 | 15.1945 | 20.0337 | 24.6671 | 27.3033 | 17.4936
5062 | 27.3208 | 23.9884 | 19.6262 | 13.5422 | 8.8361 | 6.8557 | 8.072 | 11.374 | 14.7308 | 19.2602 | 24.1701 | 26.9345 | 17.0592
5063 | 27.7668 | 24.2785 | 19.9084 | 13.6936 | 9.3212 | 7.3771 | 8.4656 | 11.9131 | 15.1945 | 20.0337 | 24.6671 | 27.3033 | 17.4936
5064 | 27.5054 | 24.0647 | 19.7992 | 13.5999 | 9.0577 | 7.0432 | 8.1843 | 11.5686 | 14.8519 | 19.5087 | 24.2965 | 27.0329 | 17.2094
5065 | 27.5054 | 24.0647 | 19.7992 | 13.5999 | 9.0577 | 7.0432 | 8.1843 | 11.5686 | 14.8519 | 19.5087 | 24.2965 | 27.0329 | 17.2094
5066 | 27.5054 | 24.0647 | 19.7992 | 13.5999 | 9.0577 | 7.0432 | 8.1843 | 11.5686 | 14.8519 | 19.5087 | 24.2965 | 27.0329 | 17.2094
5067 | 27.5913 | 24.1973 | 19.9856 | 13.7076 | 9.1968 | 7.2152 | 8.3355 | 11.7409 | 15.0034 | 19.686 | 24.5437 | 27.088 | 17.3576
5068 | 27.5913 | 24.1973 | 19.9856 | 13.7076 | 9.1968 | 7.2152 | 8.3355 | 11.7409 | 15.0034 | 19.686 | 24.5437 | 27.088 | 17.3576
5069 | 27.5913 | 24.1973 | 19.9856 | 13.7076 | 9.1968 | 7.2152 | 8.3355 | 11.7409 | 15.0034 | 19.686 | 24.5437 | 27.088 | 17.3576
5070 | 27.5913 | 24.1973 | 19.9856 | 13.7076 | 9.1968 | 7.2152 | 8.3355 | 11.7409 | 15.0034 | 19.686 | 24.5437 | 27.088 | 17.3576
5072 | 27.3783 | 24.0346 | 19.9265 | 13.7061 | 8.971 | 6.959 | 8.049 | 11.3678 | 14.7143 | 19.389 | 24.3167 | 26.9507 | 17.1469
5073 | 27.3783 | 24.0346 | 19.9265 | 13.7061 | 8.971 | 6.959 | 8.049 | 11.3678 | 14.7143 | 19.389 | 24.3167 | 26.9507 | 17.1469
5074 | 27.5913 | 24.1973 | 19.9856 | 13.7076 | 9.1968 | 7.2152 | 8.3355 | 11.7409 | 15.0034 | 19.686 | 24.5437 | 27.088 | 17.3576
5075 | 27.584 | 24.1123 | 20.0472 | 13.7375 | 9.1473 | 7.1141 | 8.1709 | 11.6082 | 14.8601 | 19.7922 | 24.4235 | 27.0856 | 17.3069
5076 | 27.584 | 24.1123 | 20.0472 | 13.7375 | 9.1473 | 7.1141 | 8.1709 | 11.6082 | 14.8601 | 19.7922 | 24.4235 | 27.0856 | 17.3069
5081 | 27.8781 | 24.4361 | 20.0797 | 13.7954 | 9.4484 | 7.4541 | 8.5734 | 12.0564 | 15.3081 | 20.2124 | 24.7727 | 27.3882 | 17.6169
5082 | 27.8781 | 24.4361 | 20.0797 | 13.7954 | 9.4484 | 7.4541 | 8.5734 | 12.0564 | 15.3081 | 20.2124 | 24.7727 | 27.3882 | 17.6169
5083 | 27.8781 | 24.4361 | 20.0797 | 13.7954 | 9.4484 | 7.4541 | 8.5734 | 12.0564 | 15.3081 | 20.2124 | 24.7727 | 27.3882 | 17.6169
5084 | 27.9539 | 24.3726 | 20.1624 | 13.8859 | 9.588 | 7.5602 | 8.6213 | 12.1248 | 15.5093 | 20.4336 | 24.7571 | 27.3813 | 17.6959
5085 | 27.9539 | 24.3726 | 20.1624 | 13.8859 | 9.588 | 7.5602 | 8.6213 | 12.1248 | 15.5093 | 20.4336 | 24.7571 | 27.3813 | 17.6959
5086 | 27.6913 | 24.2423 | 20.0872 | 13.7952 | 9.371 | 7.3992 | 8.4459 | 11.8981 | 15.1465 | 19.9732 | 24.6331 | 27.1772 | 17.4884
5087 | 27.6913 | 24.2423 | 20.0872 | 13.7952 | 9.371 | 7.3992 | 8.4459 | 11.8981 | 15.1465 | 19.9732 | 24.6331 | 27.1772 | 17.4884
5088 | 27.6913 | 24.2423 | 20.0872 | 13.7952 | 9.371 | 7.3992 | 8.4459 | 11.8981 | 15.1465 | 19.9732 | 24.6331 | 27.1772 | 17.4884
5089 | 27.584 | 24.1123 | 20.0472 | 13.7375 | 9.1473 | 7.1141 | 8.1709 | 11.6082 | 14.8601 | 19.7922 | 24.4235 | 27.0856 | 17.3069
5090 | 27.584 | 24.1123 | 20.0472 | 13.7375 | 9.1473 | 7.1141 | 8.1709 | 11.6082 | 14.8601 | 19.7922 | 24.4235 | 27.0856 | 17.3069
5091 | 27.5959 | 24.0964 | 20.097 | 13.885 | 9.1375 | 7.0442 | 8.1039 | 11.5329 | 14.9172 | 19.8879 | 24.3917 | 27.0624 | 17.3127
5092 | 27.6789 | 24.1991 | 20.1095 | 13.7956 | 9.3014 | 7.3039 | 8.2733 | 11.7768 | 15.0374 | 20.0596 | 24.5387 | 27.111 | 17.4321
5093 | 27.6913 | 24.2423 | 20.0872 | 13.7952 | 9.371 | 7.3992 | 8.4459 | 11.8981 | 15.1465 | 19.9732 | 24.6331 | 27.1772 | 17.4884
5094 | 27.6021 | 24.1277 | 20.1763 | 13.9494 | 9.745 | 7.6824 | 8.8046 | 12.3605 | 15.8857 | 20.9103 | 25.1143 | 27.3004 | 17.8049
5095 | 27.9759 | 24.5398 | 20.2523 | 13.9306 | 9.701 | 7.6509 | 8.7135 | 12.1707 | 15.6738 | 20.7122 | 24.9175 | 27.5258 | 17.8137
5096 | 27.8372 | 24.3513 | 20.2076 | 13.9038 | 9.5308 | 7.5622 | 8.5237 | 12.001 | 15.3571 | 20.2369 | 24.6414 | 27.347 | 17.625
5097 | 27.6789 | 24.1991 | 20.1095 | 13.7956 | 9.3014 | 7.3039 | 8.2733 | 11.7768 | 15.0374 | 20.0596 | 24.5387 | 27.111 | 17.4321
5098 | 27.6913 | 24.2423 | 20.0872 | 13.7952 | 9.371 | 7.3992 | 8.4459 | 11.8981 | 15.1465 | 19.9732 | 24.6331 | 27.1772 | 17.4884
5106 | 27.8372 | 24.3513 | 20.2076 | 13.9038 | 9.5308 | 7.5622 | 8.5237 | 12.001 | 15.3571 | 20.2369 | 24.6414 | 27.347 | 17.625
5107 | 27.9759 | 24.5398 | 20.2523 | 13.9306 | 9.701 | 7.6509 | 8.7135 | 12.1707 | 15.6738 | 20.7122 | 24.9175 | 27.5258 | 17.8137
5108 | 28.098 | 24.5925 | 20.3749 | 14.1286 | 9.8356 | 7.769 | 8.8165 | 12.2245 | 15.8252 | 20.8461 | 25.0905 | 27.6285 | 17.9358
5109 | 27.8372 | 24.3513 | 20.2076 | 13.9038 | 9.5308 | 7.5622 | 8.5237 | 12.001 | 15.3571 | 20.2369 | 24.6414 | 27.347 | 17.625
5110 | 28.1324 | 24.6095 | 20.4857 | 14.1604 | 9.8856 | 7.8421 | 8.965 | 12.3579 | 16.1879 | 21.1784 | 25.3735 | 27.6386 | 18.0681
5111 | 27.8936 | 24.4147 | 20.4391 | 14.2344 | 9.8415 | 7.8044 | 8.8202 | 12.0753 | 15.6725 | 20.6515 | 24.9286 | 27.3334 | 17.8424
5112 | 27.9101 | 24.4505 | 20.2558 | 14.0985 | 9.6821 | 7.6975 | 8.6839 | 12.0274 | 15.5358 | 20.4841 | 24.7493 | 27.2716 | 17.7372
5113 | 27.8221 | 24.2683 | 20.3511 | 14.2013 | 9.7618 | 7.6599 | 8.6458 | 11.8757 | 15.4127 | 20.4015 | 24.7096 | 27.189 | 17.6916
5114 | 27.5105 | 24.0418 | 20.3279 | 14.1031 | 9.3255 | 7.3468 | 8.3549 | 11.7289 | 15.1697 | 20.1154 | 24.4979 | 27.0116 | 17.4612
5115 | 27.7581 | 24.3292 | 20.5239 | 14.3206 | 9.8685 | 7.7774 | 8.8054 | 11.9319 | 15.5572 | 20.4416 | 24.8192 | 27.1508 | 17.7736
5116 | 27.8256 | 24.4303 | 20.5383 | 14.3859 | 9.9325 | 7.8762 | 8.8698 | 12.0672 | 15.6167 | 20.7542 | 24.9815 | 27.2374 | 17.8763
5117 | 27.8256 | 24.4303 | 20.5383 | 14.3859 | 9.9325 | 7.8762 | 8.8698 | 12.0672 | 15.6167 | 20.7542 | 24.9815 | 27.2374 | 17.8763
5118 | 27.8026 | 24.3737 | 20.5532 | 14.4421 | 9.965 | 7.8712 | 8.9251 | 11.9551 | 15.4911 | 20.509 | 24.8091 | 27.086 | 17.8153
5120 | 28.0677 | 24.6254 | 20.5439 | 14.3205 | 10.0022 | 7.9875 | 9.0088 | 12.2754 | 16.0861 | 21.07 | 25.2386 | 27.4361 | 18.0552
5121 | 27.8256 | 24.4303 | 20.5383 | 14.3859 | 9.9325 | 7.8762 | 8.8698 | 12.0672 | 15.6167 | 20.7542 | 24.9815 | 27.2374 | 17.8763
5125 | 27.5214 | 24.1431 | 20.1622 | 13.9729 | 9.2652 | 7.2371 | 8.1855 | 11.7301 | 15.1226 | 20.0373 | 24.4548 | 27.0103 | 17.4035
5126 | 27.5959 | 24.0964 | 20.097 | 13.885 | 9.1375 | 7.0442 | 8.1039 | 11.5329 | 14.9172 | 19.8879 | 24.3917 | 27.0624 | 17.3127
5127 | 27.6789 | 24.1991 | 20.1095 | 13.7956 | 9.3014 | 7.3039 | 8.2733 | 11.7768 | 15.0374 | 20.0596 | 24.5387 | 27.111 | 17.4321
5131 | 27.5959 | 24.0964 | 20.097 | 13.885 | 9.1375 | 7.0442 | 8.1039 | 11.5329 | 14.9172 | 19.8879 | 24.3917 | 27.0624 | 17.3127
5132 | 27.5189 | 24.0293 | 20.0224 | 13.7693 | 8.9484 | 6.9006 | 7.9614 | 11.375 | 14.7788 | 19.6252 | 24.3137 | 27.0633 | 17.1922
5133 | 27.5109 | 23.9509 | 20.0602 | 13.9069 | 9.0407 | 6.9342 | 8.1316 | 11.4917 | 14.7539 | 19.7379 | 24.282 | 26.9554 | 17.2297
5134 | 27.3656 | 23.9429 | 19.9071 | 13.6405 | 8.8363 | 6.7378 | 7.8411 | 11.164 | 14.6438 | 19.4026 | 24.2607 | 26.9372 | 17.0566
5136 | 27.3656 | 23.9429 | 19.9071 | 13.6405 | 8.8363 | 6.7378 | 7.8411 | 11.164 | 14.6438 | 19.4026 | 24.2607 | 26.9372 | 17.0566
5137 | 27.2892 | 23.8638 | 19.6085 | 13.496 | 8.6952 | 6.6511 | 7.7752 | 11.0118 | 14.4658 | 19.1095 | 24.087 | 26.6922 | 16.8955
5138 | 27.2892 | 23.8638 | 19.6085 | 13.496 | 8.6952 | 6.6511 | 7.7752 | 11.0118 | 14.4658 | 19.1095 | 24.087 | 26.6922 | 16.8955
5139 | 27.3778 | 23.8997 | 19.5094 | 13.5118 | 8.7698 | 6.7094 | 7.8859 | 10.9956 | 14.593 | 19.2493 | 24.1079 | 26.7104 | 16.9433
5140 | 27.2607 | 23.9131 | 19.6967 | 13.5088 | 8.8076 | 6.7631 | 7.8577 | 11.1934 | 14.5339 | 19.0654 | 24.0856 | 26.8325 | 16.9599
5141 | 27.2607 | 23.9131 | 19.6967 | 13.5088 | 8.8076 | 6.7631 | 7.8577 | 11.1934 | 14.5339 | 19.0654 | 24.0856 | 26.8325 | 16.9599
5142 | 27.2892 | 23.8638 | 19.6085 | 13.496 | 8.6952 | 6.6511 | 7.7752 | 11.0118 | 14.4658 | 19.1095 | 24.087 | 26.6922 | 16.8955
5144 | 27.2892 | 23.8638 | 19.6085 | 13.496 | 8.6952 | 6.6511 | 7.7752 | 11.0118 | 14.4658 | 19.1095 | 24.087 | 26.6922 | 16.8955
5151 | 27.2424 | 23.8377 | 19.3742 | 13.4266 | 8.6037 | 6.5668 | 7.737 | 10.9022 | 14.4499 | 19.0863 | 23.8945 | 26.5817 | 16.8086
5152 | 27.2218 | 23.8363 | 19.486 | 13.399 | 8.6237 | 6.5538 | 7.7383 | 11.0086 | 14.3937 | 19.0748 | 23.9516 | 26.6871 | 16.8312
5153 | 27.0565 | 23.6696 | 19.1275 | 13.313 | 8.7364 | 6.8609 | 8.0025 | 11.0107 | 14.7364 | 19.2199 | 23.9418 | 26.6207 | 16.858
5154 | 27.2424 | 23.8377 | 19.3742 | 13.4266 | 8.6037 | 6.5668 | 7.737 | 10.9022 | 14.4499 | 19.0863 | 23.8945 | 26.5817 | 16.8086
5155 | 27.2424 | 23.8377 | 19.3742 | 13.4266 | 8.6037 | 6.5668 | 7.737 | 10.9022 | 14.4499 | 19.0863 | 23.8945 | 26.5817 | 16.8086
5156 | 27.2218 | 23.8363 | 19.486 | 13.399 | 8.6237 | 6.5538 | 7.7383 | 11.0086 | 14.3937 | 19.0748 | 23.9516 | 26.6871 | 16.8312
5157 | 27.0312 | 23.7621 | 19.2807 | 13.4464 | 8.6191 | 6.6777 | 7.8445 | 11.135 | 14.6717 | 19.2213 | 23.9714 | 26.5283 | 16.8491
5158 | 27.66 | 24.2947 | 19.7044 | 13.7437 | 9.2293 | 7.3483 | 8.4486 | 11.9529 | 15.3864 | 20.066 | 24.7761 | 27.3493 | 17.4966
5159 | 27.3278 | 24.0759 | 19.598 | 13.6071 | 8.9452 | 7.0633 | 8.1949 | 11.5776 | 15.0184 | 19.5829 | 24.3982 | 27.0396 | 17.2024
5160 | 27.4734 | 23.8724 | 19.3556 | 13.6082 | 9.3069 | 7.4986 | 8.6473 | 11.9721 | 15.3513 | 20.117 | 24.8202 | 26.9906 | 17.4178
5161 | 27.5634 | 24.1072 | 19.5416 | 13.7268 | 9.1718 | 7.2585 | 8.3991 | 11.7946 | 15.2737 | 19.9068 | 24.6693 | 27.1159 | 17.3774
5162 | 27.5634 | 24.1072 | 19.5416 | 13.7268 | 9.1718 | 7.2585 | 8.3991 | 11.7946 | 15.2737 | 19.9068 | 24.6693 | 27.1159 | 17.3774
5163 | 27.4894 | 24.0805 | 19.3994 | 13.6767 | 9.1408 | 7.2268 | 8.3664 | 11.7225 | 15.1799 | 19.8593 | 24.5883 | 27.0359 | 17.3138
5164 | 27.7115 | 24.0037 | 19.2178 | 13.5972 | 9.2427 | 7.4852 | 8.6276 | 11.9404 | 15.2925 | 20.1009 | 24.6635 | 26.9308 | 17.4012
5165 | 27.7115 | 24.0037 | 19.2178 | 13.5972 | 9.2427 | 7.4852 | 8.6276 | 11.9404 | 15.2925 | 20.1009 | 24.6635 | 26.9308 | 17.4012
5166 | 27.4734 | 23.8724 | 19.3556 | 13.6082 | 9.3069 | 7.4986 | 8.6473 | 11.9721 | 15.3513 | 20.117 | 24.8202 | 26.9906 | 17.4178
5167 | 27.7115 | 24.0037 | 19.2178 | 13.5972 | 9.2427 | 7.4852 | 8.6276 | 11.9404 | 15.2925 | 20.1009 | 24.6635 | 26.9308 | 17.4012
5168 | 27.7115 | 24.0037 | 19.2178 | 13.5972 | 9.2427 | 7.4852 | 8.6276 | 11.9404 | 15.2925 | 20.1009 | 24.6635 | 26.9308 | 17.4012
5169 | 27.6649 | 24.1046 | 19.3033 | 13.5496 | 9.1956 | 7.4372 | 8.5903 | 11.898 | 15.3534 | 20.0668 | 24.7571 | 27.0885 | 17.4174
5170 | 27.4344 | 24.0545 | 19.2311 | 13.4817 | 9.1387 | 7.3823 | 8.4795 | 11.8304 | 15.384 | 20.1436 | 24.7236 | 27.1683 | 17.371
5171 | 27.3231 | 24.0651 | 19.3103 | 13.5386 | 9.0738 | 7.1973 | 8.3607 | 11.6336 | 15.1338 | 19.7703 | 24.5376 | 26.9597 | 17.242
5172 | 26.7987 | 23.6104 | 18.9951 | 13.3013 | 8.7427 | 6.9743 | 8.1817 | 11.3727 | 15.0658 | 19.596 | 24.303 | 26.5189 | 16.955
5173 | 27.0471 | 23.5777 | 19.0531 | 13.3935 | 9.1197 | 7.5057 | 8.6118 | 11.7806 | 15.0412 | 20.0804 | 24.6507 | 26.9821 | 17.237
5174 | 27.1526 | 23.9138 | 19.1744 | 13.4978 | 9.0835 | 7.3719 | 8.3697 | 11.7307 | 15.2456 | 20.1168 | 24.6993 | 27.0753 | 17.2859
5201 | 26.8667 | 23.4989 | 18.9026 | 13.2024 | 8.7272 | 6.9555 | 8.1905 | 11.3118 | 14.9584 | 19.419 | 23.9613 | 26.4768 | 16.8726
5202 | 26.8658 | 23.4344 | 18.6614 | 13.3101 | 8.799 | 7.2683 | 8.2839 | 11.7291 | 14.9416 | 19.6787 | 24.2796 | 26.6698 | 16.9935
5203 | 26.6891 | 23.2854 | 18.4059 | 13.4161 | 8.9748 | 7.3948 | 8.4168 | 11.6687 | 14.9034 | 19.691 | 24.1524 | 26.4335 | 16.9527
5204 | 26.4986 | 23.3856 | 18.5726 | 13.4411 | 9.1773 | 7.5623 | 8.5178 | 11.9286 | 15.1584 | 19.6628 | 24.0063 | 26.4398 | 17.0293
5210 | 26.5395 | 23.2517 | 18.7232 | 13.1576 | 8.6177 | 6.9161 | 8.1548 | 11.3473 | 15.2115 | 19.573 | 23.978 | 26.0463 | 16.7931
5211 | 25.8734 | 22.9358 | 18.313 | 12.8893 | 8.5134 | 6.9296 | 8.105 | 11.4612 | 15.085 | 19.3344 | 23.5979 | 25.5349 | 16.5477
5212 | 25.9451 | 22.9789 | 18.792 | 12.8281 | 8.755 | 7.2937 | 8.3436 | 11.7618 | 15.6426 | 20.0435 | 23.9138 | 25.7646 | 16.8386
5213 | 25.9451 | 22.9789 | 18.792 | 12.8281 | 8.755 | 7.2937 | 8.3436 | 11.7618 | 15.6426 | 20.0435 | 23.9138 | 25.7646 | 16.8386
5214 | 26.2125 | 23.1253 | 19.1708 | 13.0632 | 8.8662 | 7.4111 | 8.5671 | 11.9267 | 15.7104 | 20.0278 | 24.1228 | 26.0385 | 17.0202
5220 | 25.8524 | 23.0273 | 17.7312 | 12.6522 | 8.6241 | 7.158 | 8.2035 | 11.3917 | 14.8993 | 19.0198 | 23.6233 | 25.4609 | 16.4703
5221 | 25.3762 | 23.1544 | 18.2082 | 12.9076 | 8.8208 | 7.4908 | 8.3679 | 11.6839 | 15.2649 | 19.2004 | 23.2208 | 25.4658 | 16.5968
5222 | 25.5467 | 23.1373 | 17.88 | 12.7847 | 8.7251 | 7.4258 | 8.4172 | 11.5634 | 14.8927 | 19.0259 | 23.0632 | 25.2853 | 16.479
5223 | 26.1301 | 23.207 | 17.864 | 12.6496 | 8.5673 | 7.124 | 8.1082 | 11.3219 | 14.7944 | 19.0876 | 23.9298 | 25.6752 | 16.5383
5231 | 27.4858 | 23.8202 | 20.1615 | 13.837 | 9.0401 | 6.993 | 8.1971 | 11.5242 | 14.9248 | 19.8094 | 24.4068 | 27.0758 | 17.273
5232 | 27.6905 | 24.0524 | 19.9553 | 13.7816 | 8.9906 | 6.8677 | 8.0453 | 11.2994 | 14.7773 | 19.6794 | 24.5284 | 27.1452 | 17.2344
5233 | 27.6472 | 24.0417 | 20.0431 | 13.9035 | 9.0532 | 6.8381 | 8.1296 | 11.3175 | 14.9966 | 19.6159 | 24.4617 | 27.1683 | 17.268
5234 | 27.759 | 24.2061 | 20.0379 | 13.9033 | 9.2148 | 7.0623 | 8.3718 | 11.4486 | 15.235 | 19.782 | 24.6637 | 27.3089 | 17.4161
5235 | 27.9374 | 24.4391 | 20.4489 | 14.1159 | 9.4494 | 7.4782 | 8.747 | 11.9268 | 15.8368 | 20.6509 | 24.976 | 27.7613 | 17.814
5236 | 27.8109 | 24.3772 | 20.0961 | 13.961 | 9.4251 | 7.5874 | 8.7604 | 11.9224 | 15.8929 | 20.5053 | 24.8902 | 27.501 | 17.7275
5237 | 27.7406 | 24.2809 | 20.0068 | 13.9356 | 9.5544 | 7.8476 | 8.936 | 12.0447 | 16.057 | 20.6871 | 24.8159 | 27.4571 | 17.7803
5238 | 27.7551 | 24.4479 | 20.3815 | 14.1862 | 9.8694 | 7.9033 | 8.8986 | 12.3664 | 16.0929 | 20.6789 | 24.926 | 27.5961 | 17.9252
5240 | 27.3778 | 23.8997 | 19.5094 | 13.5118 | 8.7698 | 6.7094 | 7.8859 | 10.9956 | 14.593 | 19.2493 | 24.1079 | 26.7104 | 16.9433
5241 | 27.5409 | 24.2295 | 19.882 | 13.708 | 9.0193 | 6.8759 | 8.1234 | 11.2475 | 14.9487 | 19.7454 | 24.5108 | 27.1193 | 17.2459
5242 | 27.3343 | 23.9067 | 19.4898 | 13.4959 | 8.9517 | 6.8757 | 8.1207 | 11.0755 | 14.8979 | 19.424 | 24.1996 | 26.8959 | 17.0556
5243 | 27.3343 | 23.9067 | 19.4898 | 13.4959 | 8.9517 | 6.8757 | 8.1207 | 11.0755 | 14.8979 | 19.424 | 24.1996 | 26.8959 | 17.0556
5244 | 27.5493 | 24.1459 | 19.7664 | 13.6645 | 9.074 | 7.0154 | 8.2607 | 11.3872 | 15.3526 | 19.9586 | 24.659 | 27.0802 | 17.3261
5245 | 27.3343 | 23.9067 | 19.4898 | 13.4959 | 8.9517 | 6.8757 | 8.1207 | 11.0755 | 14.8979 | 19.424 | 24.1996 | 26.8959 | 17.0556
5250 | 27.2192 | 23.9145 | 19.4457 | 13.3871 | 8.9188 | 7.0072 | 8.2556 | 11.1872 | 15.0061 | 19.4754 | 24.1815 | 26.8552 | 17.0711
5251 | 27.1957 | 23.7086 | 19.3672 | 13.4552 | 9.0971 | 7.183 | 8.4099 | 11.4136 | 15.4304 | 19.8427 | 24.2513 | 26.6782 | 17.1694
5252 | 27.3272 | 23.81 | 19.5616 | 13.6056 | 9.3325 | 7.4939 | 8.5933 | 11.7258 | 15.7496 | 20.2971 | 24.3459 | 26.847 | 17.3908
5253 | 27.6672 | 24.255 | 20.0011 | 13.9219 | 9.6003 | 7.7482 | 8.7722 | 12.0195 | 15.9204 | 20.3725 | 24.6773 | 27.3379 | 17.6911
5254 | 27.3384 | 23.8731 | 19.8787 | 13.4597 | 9.3201 | 7.7034 | 8.751 | 12.0074 | 15.8671 | 20.3771 | 24.322 | 26.7486 | 17.4705
5255 | 26.9026 | 23.4246 | 19.3391 | 13.2892 | 9.3198 | 7.6836 | 8.5244 | 11.9343 | 15.7744 | 20.1834 | 24.1873 | 26.3284 | 17.2409
5256 | 26.4704 | 23.3143 | 19.4339 | 13.3377 | 8.9309 | 7.4634 | 8.5311 | 11.8418 | 15.9489 | 19.8575 | 23.9007 | 25.8053 | 17.0697
5259 | 27.1175 | 23.7403 | 19.4685 | 13.6011 | 9.047 | 7.5592 | 8.6467 | 12.0168 | 15.798 | 20.1174 | 24.3244 | 26.3222 | 17.3133
5260 | 27.5436 | 24.1887 | 19.8123 | 13.8943 | 9.5291 | 7.6982 | 8.6721 | 12.0018 | 15.8485 | 20.3424 | 24.8455 | 27.2948 | 17.6393
5261 | 27.695 | 24.2952 | 19.8492 | 14.0703 | 9.6208 | 7.8074 | 8.6995 | 11.8903 | 15.6538 | 20.4275 | 24.6729 | 27.282 | 17.6637
5262 | 26.8511 | 23.9567 | 18.9463 | 12.9046 | 8.4987 | 6.8287 | 7.5411 | 10.828 | 14.2904 | 19.1392 | 23.9607 | 26.5414 | 16.6906
5263 | 25.8992 | 23.5246 | 18.1316 | 12.3496 | 8.1049 | 6.5681 | 7.3066 | 10.4687 | 13.841 | 18.3081 | 23.094 | 25.5904 | 16.0989
5264 | 27.1977 | 24.0917 | 19.6975 | 13.5277 | 9.1231 | 7.4528 | 8.3755 | 11.6026 | 15.4654 | 20.4246 | 24.8332 | 27.0646 | 17.4047
5265 | 27.0883 | 24.1039 | 19.6695 | 13.7333 | 9.2475 | 7.4982 | 8.315 | 11.5487 | 15.3337 | 20.1886 | 24.5005 | 26.9668 | 17.3495
5266 | 27.1336 | 24.1208 | 19.5434 | 13.7212 | 9.2365 | 7.4356 | 8.3317 | 11.4772 | 15.1949 | 20.2075 | 24.4959 | 26.933 | 17.3193
5267 | 27.1859 | 23.8974 | 19.5379 | 13.6793 | 9.0974 | 7.2743 | 8.174 | 11.5343 | 15.0604 | 20.0418 | 24.5257 | 27.4051 | 17.2845
5268 | 27.0071 | 24.0061 | 19.2862 | 13.2341 | 8.759 | 6.9964 | 7.8665 | 11.1125 | 14.6634 | 19.5675 | 24.3528 | 27.0738 | 16.9938
5269 | 26.9405 | 24.2264 | 19.6764 | 13.7184 | 9.1985 | 7.1966 | 8.0302 | 11.3246 | 14.8503 | 19.7227 | 24.6273 | 27.1536 | 17.2221
5270 | 26.9189 | 23.9295 | 19.3133 | 13.207 | 8.7301 | 7.0753 | 7.9128 | 11.107 | 14.7485 | 19.6058 | 24.3496 | 26.9454 | 16.9869
5271 | 26.4262 | 23.9075 | 18.6443 | 12.5966 | 8.3399 | 6.7654 | 7.4417 | 10.7954 | 14.1635 | 18.9412 | 23.7589 | 26.1492 | 16.4942
5272 | 26.4484 | 23.7443 | 18.2587 | 12.5823 | 8.3089 | 6.6879 | 7.5967 | 10.8365 | 14.2546 | 18.8269 | 23.6554 | 25.9107 | 16.4259
5275 | 26.7156 | 23.793 | 18.8434 | 12.8461 | 8.5526 | 6.9929 | 7.8317 | 11.1907 | 14.6351 | 19.5051 | 24.047 | 26.6389 | 16.7994
5276 | 26.3972 | 23.637 | 18.2914 | 12.2637 | 8.0435 | 6.736 | 7.5057 | 10.9757 | 14.1356 | 18.8698 | 23.4927 | 25.8386 | 16.3489
5277 | 25.9443 | 23.1875 | 17.6141 | 12.0447 | 7.7886 | 6.4534 | 7.181 | 10.3882 | 13.7427 | 18.1444 | 22.7263 | 25.3844 | 15.8833
5278 | 25.6691 | 22.772 | 17.314 | 11.6468 | 7.5347 | 6.2545 | 7.0697 | 10.3764 | 13.9035 | 18.2539 | 22.7592 | 25.2384 | 15.7327
5279 | 25.7913 | 22.6979 | 17.4002 | 11.6703 | 7.5719 | 6.3242 | 7.0157 | 10.3177 | 13.7627 | 18.2809 | 22.8072 | 25.236 | 15.7397
5280 | 25.9265 | 23.0933 | 17.7206 | 11.8788 | 7.6941 | 6.4501 | 7.1358 | 10.2548 | 13.8489 | 18.2813 | 23.1693 | 25.1777 | 15.8859
5290 | 25.1 | 22.0785 | 16.7797 | 11.3945 | 7.409 | 6.1603 | 6.9911 | 10.2051 | 13.7617 | 17.932 | 22.3776 | 24.5323 | 15.3935
5291 | 24.8659 | 21.9054 | 16.5849 | 11.3608 | 7.4313 | 6.2002 | 7.0165 | 10.2057 | 13.5563 | 17.8719 | 22.4986 | 24.5941 | 15.341
5301 | 27.5658 | 24.4335 | 20.1278 | 14.1454 | 9.6964 | 7.7724 | 8.74 | 11.9609 | 15.6537 | 20.477 | 24.8701 | 27.6677 | 17.7592
5302 | 26.9843 | 23.8464 | 20.1038 | 13.9295 | 9.4651 | 7.5134 | 8.4822 | 11.9044 | 15.7441 | 20.1931 | 24.5648 | 27.6286 | 17.53
5303 | 27.7609 | 24.4823 | 20.5895 | 14.6211 | 10.1074 | 8.0391 | 8.859 | 12.1803 | 16.1656 | 21.2846 | 25.3944 | 27.8112 | 18.1079
5304 | 27.6947 | 24.5662 | 20.6607 | 14.7019 | 10.153 | 8.0221 | 8.8065 | 12.1776 | 16.3219 | 21.3855 | 25.4053 | 27.6534 | 18.1291
5307 | 27.9015 | 24.5121 | 20.2973 | 14.2749 | 9.8154 | 7.8206 | 8.9371 | 12.1209 | 15.8961 | 20.6347 | 25.0013 | 27.9162 | 17.9273
5308 | 28.0481 | 24.6002 | 20.8018 | 14.742 | 10.1404 | 8.1723 | 9.2385 | 12.528 | 16.3474 | 21.1302 | 25.2195 | 27.979 | 18.2456
5309 | 27.9609 | 24.6453 | 20.406 | 14.4986 | 9.9394 | 7.9089 | 8.9292 | 12.1282 | 16.1188 | 20.6667 | 25.0271 | 27.8895 | 18.0099
5311 | 28.034 | 24.657 | 21.0702 | 15.0607 | 10.4848 | 8.3816 | 9.3346 | 12.7817 | 16.6035 | 21.6416 | 25.3494 | 27.9695 | 18.4474
5320 | 28.2279 | 24.4386 | 21.2123 | 15.0182 | 10.5816 | 8.5925 | 9.6548 | 12.8686 | 16.9583 | 21.7884 | 25.4271 | 27.9826 | 18.5626
5321 | 28.0368 | 24.6806 | 21.4817 | 15.165 | 10.6122 | 8.56 | 9.6096 | 12.9747 | 17.1356 | 21.8902 | 25.4132 | 28.0752 | 18.6362
5322 | 28.1166 | 24.6001 | 21.3445 | 15.2604 | 10.6127 | 8.5184 | 9.4943 | 12.8407 | 16.9538 | 21.7299 | 25.3891 | 28.1708 | 18.586
5330 | 28.1739 | 24.4391 | 21.3522 | 15.3151 | 10.531 | 8.4136 | 9.5059 | 12.8939 | 16.6432 | 21.6097 | 25.1064 | 28.0382 | 18.5018
5331 | 28.1461 | 24.7225 | 21.412 | 15.1928 | 10.5146 | 8.4179 | 9.5855 | 13.0144 | 16.8857 | 21.7645 | 25.3106 | 28.0794 | 18.5872
5332 | 28.089 | 24.5773 | 21.4341 | 15.3172 | 10.5583 | 8.3385 | 9.5123 | 12.9453 | 16.8593 | 21.5896 | 25.345 | 28.0047 | 18.5475
5333 | 28.1076 | 24.6045 | 21.0639 | 15.1186 | 10.5092 | 8.3316 | 9.4192 | 12.7503 | 16.7391 | 21.6543 | 25.4133 | 28.0295 | 18.4784
5340 | 28.3022 | 24.5803 | 21.3444 | 15.4256 | 10.7285 | 8.547 | 9.5772 | 13.0792 | 16.8323 | 21.9703 | 25.5876 | 28.1227 | 18.6748
5341 | 28.263 | 24.6356 | 21.412 | 15.3578 | 10.685 | 8.5047 | 9.565 | 13.0657 | 16.8946 | 21.954 | 25.4756 | 28.3292 | 18.6785
5342 | 28.2916 | 24.5687 | 21.2768 | 15.4124 | 10.5423 | 8.4082 | 9.5095 | 12.9708 | 16.7688 | 21.6559 | 25.3418 | 28.0778 | 18.5687
5343 | 28.2205 | 24.4702 | 21.3427 | 15.2523 | 10.4589 | 8.3111 | 9.4019 | 13.039 | 16.788 | 21.7904 | 25.4619 | 28.2758 | 18.5677
5344 | 28.3184 | 24.5516 | 21.2801 | 15.3111 | 10.5701 | 8.37 | 9.4821 | 13.0687 | 16.7836 | 21.784 | 25.5091 | 28.2312 | 18.605
5345 | 28.2721 | 24.526 | 21.4523 | 15.3084 | 10.609 | 8.3994 | 9.4853 | 12.9666 | 16.7318 | 21.7404 | 25.4124 | 28.1222 | 18.5855
5346 | 28.1859 | 24.6105 | 21.5652 | 15.3356 | 10.5193 | 8.3266 | 9.527 | 13.0175 | 16.8164 | 21.6957 | 25.4245 | 28.2597 | 18.607
5350 | 27.849 | 24.4049 | 20.5249 | 14.2267 | 9.7434 | 7.6254 | 8.6313 | 11.6355 | 15.1465 | 20.1494 | 24.671 | 27.1849 | 17.6494
5351 | 27.8003 | 24.3197 | 20.428 | 14.0065 | 9.3726 | 7.3045 | 8.401 | 11.6099 | 15.1324 | 19.8704 | 24.6821 | 27.3985 | 17.5272
5352 | 28.0144 | 24.1838 | 20.4937 | 14.2519 | 9.6645 | 7.7026 | 8.638 | 11.8475 | 15.5311 | 20.1951 | 24.8389 | 27.4428 | 17.7337
5353 | 27.8494 | 24.5553 | 20.5017 | 14.3884 | 9.8739 | 8.0825 | 9.2061 | 12.4052 | 16.2652 | 21.1476 | 25.0686 | 27.8024 | 18.0955
5354 | 27.9768 | 24.6574 | 20.7378 | 14.4541 | 10.0504 | 8.2015 | 9.2667 | 12.5902 | 16.2503 | 21.139 | 25.102 | 27.9548 | 18.1984
5355 | 28.0043 | 24.4614 | 20.6619 | 14.5964 | 9.9986 | 7.9106 | 8.9422 | 12.2276 | 15.9421 | 20.6776 | 24.8966 | 27.3669 | 17.9738
5356 | 27.9608 | 24.5484 | 20.7291 | 14.7047 | 10.238 | 8.4018 | 9.4568 | 12.7195 | 16.4922 | 21.257 | 24.9567 | 27.5121 | 18.2481
5357 | 28.0843 | 24.7076 | 21.3042 | 14.9846 | 10.3682 | 8.3003 | 9.412 | 12.7152 | 16.6667 | 21.4767 | 25.3046 | 27.9572 | 18.4401
5360 | 27.9458 | 24.3484 | 20.7193 | 14.4915 | 9.9316 | 7.9508 | 8.9564 | 11.975 | 15.5341 | 20.2513 | 24.6806 | 27.2729 | 17.8381
5371 | 27.8312 | 24.5022 | 20.6519 | 14.5752 | 9.962 | 7.8424 | 8.8133 | 11.7946 | 15.2598 | 20.2438 | 24.6452 | 26.9353 | 17.7547
5372 | 27.6052 | 24.3975 | 20.7486 | 14.5816 | 9.9373 | 7.8491 | 8.8855 | 11.9399 | 15.442 | 20.2508 | 24.5455 | 27.0328 | 17.768
5373 | 27.9709 | 24.4468 | 20.7097 | 14.7117 | 10.1665 | 8.0357 | 9.1091 | 12.2242 | 15.6624 | 20.5378 | 24.8681 | 27.2215 | 17.972
5374 | 28.0331 | 24.6567 | 21.1689 | 14.9506 | 10.4143 | 8.5917 | 9.6403 | 12.8989 | 16.8663 | 21.5526 | 25.1485 | 27.399 | 18.4434
5381 | 27.9953 | 24.5655 | 21.2233 | 14.8971 | 10.5698 | 8.6767 | 9.7398 | 13.0635 | 17.101 | 21.7591 | 25.2895 | 27.7782 | 18.5549
5400 | 27.8136 | 24.4078 | 20.6752 | 14.5824 | 10.0054 | 7.9347 | 8.9049 | 11.8871 | 15.4249 | 20.4364 | 24.6738 | 27.0094 | 17.813
5401 | 27.681 | 24.5182 | 20.898 | 14.7602 | 10.0474 | 8.0108 | 9.0322 | 11.7708 | 15.3666 | 20.4422 | 24.5299 | 26.9322 | 17.8325
5410 | 27.6551 | 24.4647 | 20.7836 | 14.5786 | 10.0034 | 8.0192 | 9.0153 | 11.8705 | 15.4303 | 20.3587 | 24.6016 | 26.9412 | 17.8102
5411 | 27.6084 | 24.3349 | 20.7898 | 14.6884 | 9.9994 | 7.9563 | 8.9407 | 11.9524 | 15.3588 | 20.2652 | 24.6764 | 26.9644 | 17.7946
5412 | 27.6566 | 24.5131 | 20.9851 | 14.8322 | 10.0748 | 8.0508 | 9.0147 | 11.9896 | 15.3155 | 20.4506 | 24.8615 | 27.1576 | 17.9085
5413 | 27.8992 | 24.4755 | 21.2481 | 15.0129 | 10.2906 | 8.1977 | 9.2599 | 12.4841 | 16.0909 | 20.9533 | 25.0366 | 27.3101 | 18.1883
5414 | 27.7385 | 24.4724 | 21.1297 | 14.979 | 10.3405 | 8.2379 | 9.1978 | 12.23 | 15.5089 | 20.67 | 24.9428 | 27.2419 | 18.0574
5415 | 27.7787 | 24.5571 | 21.2979 | 15.0691 | 10.425 | 8.1841 | 9.2638 | 12.3346 | 15.7247 | 20.9569 | 25.1876 | 27.514 | 18.1911
5416 | 27.8209 | 24.6962 | 21.4343 | 15.0728 | 10.507 | 8.2261 | 9.33 | 12.3523 | 15.9786 | 21.1518 | 24.9632 | 27.4112 | 18.2454
5417 | 28.1186 | 24.6147 | 21.3952 | 15.0444 | 10.6645 | 8.8168 | 9.825 | 13.0914 | 17.1779 | 21.9441 | 25.2975 | 27.9737 | 18.6637
5419 | 28.0673 | 24.607 | 21.6915 | 15.5611 | 10.7501 | 8.9813 | 10.0328 | 13.3005 | 17.3085 | 21.9608 | 25.4522 | 27.9418 | 18.8046
5421 | 28.4467 | 24.8402 | 21.8306 | 15.7092 | 10.8097 | 9.0184 | 10.1044 | 13.384 | 17.4662 | 22.2319 | 25.5441 | 28.3275 | 18.9761
5422 | 28.5866 | 24.9342 | 22.5072 | 16.2414 | 11.2341 | 9.3173 | 10.2973 | 13.7668 | 17.9011 | 23.0597 | 25.9416 | 28.522 | 19.3591
5431 | 28.834 | 24.8522 | 22.3186 | 16.4706 | 11.6525 | 9.5785 | 10.6892 | 13.8529 | 18.06 | 22.9272 | 26.0728 | 28.3736 | 19.4735
5433 | 28.7032 | 24.8982 | 22.5984 | 16.748 | 11.8929 | 9.7939 | 10.9758 | 14.1482 | 18.4869 | 23.1363 | 26.2103 | 28.7958 | 19.699
5434 | 28.7356 | 25.0881 | 22.4324 | 16.9018 | 12.0698 | 9.9617 | 11.1049 | 14.2401 | 18.575 | 23.3247 | 26.3939 | 28.8451 | 19.8061
5440 | 28.8257 | 25.0415 | 22.511 | 16.6458 | 11.8254 | 9.8543 | 10.8743 | 14.238 | 18.7249 | 23.321 | 26.2127 | 28.8529 | 19.744
5451 | 27.805 | 24.5227 | 21.1121 | 14.8579 | 10.2598 | 8.0977 | 9.1544 | 12.0692 | 15.4486 | 20.6071 | 25.0421 | 27.3632 | 18.0283
5452 | 27.7615 | 24.3642 | 21.082 | 14.9067 | 10.0799 | 7.8971 | 9.0743 | 12.1865 | 15.6025 | 20.6668 | 25.2067 | 27.5973 | 18.0355
5453 | 27.7916 | 24.7593 | 21.3876 | 15.1912 | 10.4326 | 8.2698 | 9.1825 | 12.1801 | 15.7027 | 20.9199 | 25.3417 | 27.553 | 18.226
5454 | 27.9585 | 24.7446 | 21.6262 | 15.4308 | 10.5507 | 8.559 | 9.3394 | 12.4284 | 16.0872 | 21.186 | 24.9401 | 27.3655 | 18.3514
5460 | 27.8566 | 24.6022 | 20.9233 | 14.7384 | 10.1721 | 8.1467 | 9.1526 | 12.0455 | 15.6007 | 20.5547 | 24.4976 | 26.9375 | 17.9357
5461 | 27.8343 | 24.6228 | 21.0505 | 14.8418 | 10.3247 | 8.2355 | 9.1097 | 12.0698 | 15.6429 | 20.6587 | 24.8344 | 27.1429 | 18.0307
5462 | 27.8703 | 24.4987 | 21.2285 | 15.0689 | 10.3201 | 8.1786 | 9.0788 | 12.0275 | 15.6624 | 20.6405 | 24.6992 | 27.1502 | 18.0353
5464 | 28.1396 | 24.7388 | 21.3883 | 15.2583 | 10.5063 | 8.411 | 9.3663 | 12.3517 | 15.7611 | 21.0511 | 24.8235 | 27.4694 | 18.2721
5470 | 27.9137 | 24.8961 | 21.6562 | 15.5044 | 10.6959 | 8.6008 | 9.4074 | 12.4518 | 16.134 | 21.0094 | 24.8129 | 27.4374 | 18.3767
5472 | 27.9487 | 24.8302 | 21.612 | 15.6418 | 10.7811 | 8.7112 | 9.5453 | 12.4323 | 16.1233 | 21.1843 | 24.8197 | 27.414 | 18.4203
5473 | 27.9435 | 24.8519 | 21.6479 | 15.6277 | 10.8075 | 8.7678 | 9.6281 | 12.7236 | 16.4623 | 21.2681 | 24.8472 | 27.5111 | 18.5072
5480 | 27.7336 | 24.4993 | 21.466 | 15.5285 | 10.7139 | 8.8325 | 9.8263 | 12.8586 | 16.4662 | 21.4717 | 25.0417 | 27.6072 | 18.5038
5481 | 28.2425 | 24.9606 | 21.8715 | 15.9519 | 11.0439 | 9.0267 | 10.0565 | 12.9834 | 16.815 | 21.9007 | 25.016 | 27.7649 | 18.8028
5482 | 28.451 | 25.0222 | 22.133 | 16.1686 | 11.2524 | 9.1712 | 10.2202 | 13.3267 | 17.38 | 22.3394 | 25.4385 | 27.9434 | 19.0706
5483 | 28.0409 | 24.4145 | 21.5731 | 15.6662 | 10.6272 | 8.7272 | 9.7995 | 12.8927 | 16.7305 | 21.6843 | 25.1108 | 27.7506 | 18.5848
5485 | 28.5394 | 24.9406 | 22.1659 | 16.3645 | 11.6272 | 9.5711 | 10.5697 | 13.6735 | 17.8504 | 22.816 | 25.944 | 28.3736 | 19.3697
5490 | 27.9876 | 24.9414 | 21.907 | 15.8784 | 10.9214 | 8.9126 | 9.7861 | 12.8663 | 16.6336 | 21.5396 | 24.931 | 27.6102 | 18.6596
5491 | 28.0086 | 24.9014 | 21.9493 | 15.9259 | 10.8801 | 8.9037 | 9.626 | 12.7573 | 16.648 | 21.5605 | 25.1877 | 27.6014 | 18.6625
5495 | 28.1829 | 24.9413 | 21.5643 | 15.5728 | 10.821 | 8.7657 | 9.8856 | 13.0841 | 17.16 | 21.6227 | 25.4148 | 27.9292 | 18.7454
5501 | 28.0544 | 24.815 | 20.7277 | 14.6264 | 10.2172 | 8.1646 | 9.1787 | 12.2249 | 16.0669 | 20.8559 | 25.0178 | 27.2846 | 18.1028
5502 | 27.8993 | 24.4076 | 20.6332 | 14.6134 | 10.1049 | 8.0831 | 9.0518 | 12.0709 | 15.7367 | 20.7213 | 24.6826 | 27.2272 | 17.936
5510 | 28.0641 | 24.8813 | 21.1881 | 14.9599 | 10.4203 | 8.5732 | 9.3736 | 12.5677 | 16.3406 | 21.0112 | 24.8861 | 27.3633 | 18.3025
5520 | 28.122 | 24.8812 | 21.4172 | 15.298 | 10.7524 | 8.7004 | 9.6411 | 12.6113 | 16.1861 | 21.1258 | 25.0768 | 27.4428 | 18.4379
5521 | 28.2096 | 25.0996 | 21.4803 | 15.4744 | 10.781 | 8.7711 | 9.6249 | 12.5813 | 16.3247 | 21.3239 | 24.8531 | 27.6552 | 18.5149
5522 | 28.3508 | 25.0719 | 21.2917 | 15.3917 | 10.8281 | 8.9167 | 9.8549 | 13.0406 | 16.8711 | 21.6899 | 25.2598 | 27.609 | 18.6813
5523 | 28.5972 | 25.2732 | 21.5323 | 15.6597 | 11.0066 | 8.9834 | 9.9092 | 13.0378 | 17.0789 | 21.8858 | 25.4406 | 27.9557 | 18.8634
5540 | 28.1172 | 24.4674 | 21.0447 | 15.5518 | 10.8885 | 9.0199 | 10.0609 | 13.125 | 16.7341 | 21.3863 | 24.911 | 27.3957 | 18.5585
5550 | 28.2158 | 24.909 | 20.8552 | 14.6199 | 10.4309 | 8.3847 | 9.3286 | 12.5318 | 16.3001 | 21.0786 | 25.1953 | 27.4174 | 18.2723
5552 | 28.4005 | 25.1463 | 21.1672 | 15.1184 | 10.5379 | 8.5429 | 9.4327 | 12.5034 | 16.124 | 21.1068 | 25.0409 | 27.2998 | 18.3684
5554 | 28.4692 | 25.3976 | 20.9667 | 15.0478 | 10.7396 | 8.8526 | 9.7543 | 12.9682 | 16.5638 | 21.3518 | 25.2617 | 27.3257 | 18.5583
5555 | 28.4326 | 25.2022 | 21.2814 | 15.2458 | 10.6364 | 8.7579 | 9.6165 | 12.7707 | 16.5072 | 21.5022 | 25.0711 | 27.3253 | 18.5291
5556 | 28.5567 | 25.3874 | 20.7761 | 15.1232 | 10.6981 | 8.9011 | 9.8923 | 13.0424 | 16.4338 | 21.4202 | 25.1111 | 27.2433 | 18.5488
5558 | 28.5043 | 25.2554 | 20.5201 | 14.9375 | 10.57 | 8.8022 | 9.7449 | 12.9903 | 16.4416 | 21.2271 | 25.2649 | 27.444 | 18.4752
5560 | 28.4207 | 25.194 | 21.2234 | 15.1666 | 10.621 | 8.6705 | 9.5634 | 12.651 | 16.4796 | 21.5364 | 25.2106 | 27.3461 | 18.5069
5570 | 28.1326 | 25.0756 | 20.8772 | 14.8052 | 10.3887 | 8.5126 | 9.4087 | 12.3511 | 16.2449 | 20.954 | 24.7217 | 26.7934 | 18.1888
5571 | 27.2885 | 24.7441 | 20.255 | 14.3053 | 10.0315 | 8.1592 | 9.2241 | 12.5502 | 16.9342 | 20.5422 | 24.0362 | 26.0714 | 17.8452
5572 | 28.3332 | 25.1033 | 20.5544 | 14.9604 | 10.4258 | 8.6091 | 9.5014 | 12.6712 | 16.2801 | 21.1578 | 25.1527 | 26.9241 | 18.3061
5573 | 28.2091 | 25.0997 | 20.2328 | 14.6691 | 10.2422 | 8.3844 | 9.2726 | 12.2404 | 15.8747 | 20.6705 | 24.8654 | 26.7132 | 18.0395
5575 | 27.2657 | 24.1372 | 19.1114 | 14.0332 | 9.6777 | 8.1384 | 9.2348 | 12.4675 | 15.9696 | 20.0518 | 24.2539 | 26.7829 | 17.5937
5576 | 27.116 | 24.624 | 19.3333 | 13.6639 | 9.7155 | 8.1372 | 9.0207 | 11.9589 | 15.7142 | 20.2218 | 24.4688 | 25.903 | 17.4898
5577 | 27.2447 | 24.159 | 19.1743 | 13.5 | 9.2028 | 7.8055 | 8.8529 | 12.3728 | 15.8757 | 20.3961 | 24.7165 | 26.7978 | 17.5082
5580 | 27.5772 | 24.7621 | 19.7983 | 14.211 | 10.0653 | 8.2785 | 9.1419 | 12.1068 | 16.0325 | 20.5788 | 24.4421 | 26.1599 | 17.7629
5581 | 27.3025 | 24.5076 | 20.1046 | 14.1922 | 9.8155 | 7.9497 | 9.0627 | 12.3839 | 16.8001 | 20.4904 | 24.3909 | 26.4043 | 17.7837
5582 | 26.8999 | 24.3151 | 20.0267 | 14.0533 | 9.7171 | 7.8896 | 9.0165 | 12.3243 | 16.6353 | 20.3226 | 24.4044 | 26.2072 | 17.651
5583 | 27.0868 | 24.2515 | 19.9602 | 13.9494 | 9.6368 | 7.8475 | 8.9478 | 12.1461 | 16.6289 | 20.3441 | 24.7536 | 26.8123 | 17.6971
5600 | 27.6619 | 24.8422 | 20.7127 | 15.0251 | 10.7455 | 8.8606 | 9.9775 | 13.1499 | 17.1484 | 21.2656 | 25.0043 | 26.8505 | 18.437
5601 | 28.8077 | 25.4629 | 21.7212 | 16.1641 | 11.4818 | 9.6303 | 10.7936 | 13.9216 | 17.9019 | 22.4747 | 25.7592 | 28.2207 | 19.3616
5602 | 27.2366 | 24.2717 | 19.697 | 14.2038 | 10.2072 | 8.7322 | 9.6795 | 12.8593 | 17.1298 | 21.202 | 24.5885 | 26.371 | 18.0149
5603 | 27.2349 | 24.1015 | 19.6833 | 14.145 | 9.9948 | 8.6306 | 9.5096 | 12.8808 | 16.9531 | 21.0088 | 24.6336 | 26.3189 | 17.9246
5604 | 26.8402 | 24.0534 | 19.6698 | 14.148 | 9.6972 | 8.3042 | 9.4854 | 12.9288 | 17.0157 | 20.9585 | 24.5189 | 26.1724 | 17.816
5605 | 26.6088 | 23.6997 | 18.8394 | 13.5124 | 9.5084 | 8.3045 | 9.3061 | 12.2533 | 15.8867 | 20.2966 | 24.1203 | 25.9549 | 17.3576
5606 | 25.8412 | 23.2838 | 18.8321 | 13.399 | 9.2412 | 7.8568 | 9.0465 | 12.0332 | 15.9688 | 19.9145 | 23.6613 | 25.5886 | 17.0556
5607 | 27.5973 | 24.4725 | 20.5793 | 14.6897 | 10.0781 | 8.4283 | 9.6993 | 12.7893 | 16.3639 | 21.2318 | 24.878 | 26.9477 | 18.1463
5608 | 28.2269 | 25.2097 | 21.9377 | 15.9655 | 11.0003 | 9.0429 | 10.2536 | 13.6356 | 18.0163 | 22.3363 | 25.4693 | 27.8417 | 19.078
5609 | 28.2541 | 25.3263 | 21.78 | 15.844 | 11.1528 | 9.2103 | 10.3129 | 13.6954 | 17.921 | 22.3157 | 25.4375 | 27.8865 | 19.0947
5630 | 26.9151 | 24.0109 | 19.374 | 13.7197 | 9.5796 | 8.1663 | 9.1935 | 12.2594 | 15.5357 | 20.3264 | 24.3461 | 26.2327 | 17.4716
5631 | 26.8252 | 24.5581 | 19.9406 | 14.4382 | 10.061 | 8.5672 | 9.5064 | 12.5195 | 15.6891 | 20.821 | 24.1834 | 25.8246 | 17.7445
5633 | 28.1222 | 25.1197 | 20.6502 | 14.8356 | 10.4434 | 8.8433 | 9.7415 | 12.6576 | 16.2237 | 21.582 | 24.9053 | 27.0601 | 18.3487
5640 | 27.4106 | 24.094 | 19.5763 | 14.3224 | 10.3678 | 8.8005 | 9.6218 | 12.5802 | 16.4884 | 20.8924 | 24.5646 | 26.3258 | 17.9204
5641 | 28.5885 | 25.5771 | 21.0991 | 15.6712 | 11.0425 | 9.3188 | 10.3776 | 13.3254 | 17.1659 | 21.9525 | 25.2632 | 27.3693 | 18.8959
5642 | 28.0257 | 24.6346 | 20.545 | 14.8537 | 10.4227 | 8.6945 | 9.6561 | 12.7102 | 16.7769 | 21.4388 | 25.0876 | 26.9772 | 18.3186
5650 | 28.5319 | 25.2571 | 21.0633 | 15.5647 | 10.9307 | 9.2211 | 10.317 | 13.3002 | 17.204 | 22.0996 | 25.0808 | 27.0736 | 18.8037
5652 | 28.5405 | 25.2432 | 21.1362 | 15.6877 | 11.0051 | 9.2546 | 10.2612 | 13.2429 | 17.1497 | 21.9534 | 25.1751 | 27.1279 | 18.8148
5654 | 28.6289 | 25.2694 | 21.2107 | 15.65 | 10.9862 | 9.3884 | 10.414 | 13.3004 | 17.14 | 22.1154 | 25.2654 | 27.375 | 18.8953
5670 | 28.4156 | 25.322 | 21.1437 | 14.7767 | 10.3137 | 8.6068 | 9.8255 | 13.1109 | 16.7023 | 21.6925 | 25.5151 | 27.3721 | 18.5664
5680 | 28.446 | 25.5031 | 21.2016 | 15.6136 | 11.1277 | 9.5144 | 10.5231 | 13.6779 | 17.2855 | 22.1951 | 25.3198 | 27.3044 | 18.976
5690 | 28.1986 | 25.0962 | 21.5726 | 17.1494 | 12.9767 | 11.1918 | 12.2807 | 15.1473 | 19.2531 | 23.1688 | 26.2145 | 27.4038 | 19.9711
5700 | 28.6578 | 25.3121 | 22.1953 | 16.4019 | 11.4846 | 9.4344 | 10.5153 | 13.7759 | 17.7826 | 22.6645 | 26.1987 | 28.5367 | 19.4133
5710 | 29.2585 | 25.868 | 22.8774 | 17.6934 | 13.2489 | 11.0868 | 12.3591 | 15.7302 | 19.6144 | 23.8793 | 26.3982 | 28.7688 | 20.5652
5720 | 29.2433 | 25.7103 | 22.6832 | 17.3356 | 12.9339 | 10.8669 | 11.9543 | 15.2066 | 19.1568 | 23.817 | 26.442 | 29.0409 | 20.3659
5722 | 29.0795 | 25.5693 | 23.084 | 17.4995 | 13.2231 | 11.3184 | 12.4424 | 15.8648 | 19.9859 | 24.0958 | 26.7006 | 29.0373 | 20.6584
5723 | 28.7083 | 25.5191 | 22.8932 | 17.9941 | 13.9449 | 12.1275 | 13.176 | 16.4968 | 20.4357 | 24.1253 | 26.7749 | 28.1268 | 20.8602
5724 | 28.2142 | 25.3417 | 23.5562 | 18.4792 | 14.7121 | 12.8098 | 13.7254 | 17.3828 | 21.2429 | 24.5111 | 26.7209 | 27.2653 | 21.1635
5725 | 29.3008 | 25.9121 | 23.2266 | 17.8878 | 13.3419 | 11.26 | 12.4145 | 15.7714 | 19.8626 | 24.0806 | 26.6469 | 29.1694 | 20.7396
5731 | 28.7097 | 25.2922 | 23.7068 | 18.4326 | 14.0242 | 12.1879 | 13.271 | 17.0456 | 20.6163 | 23.8905 | 26.5852 | 28.2895 | 21.0043
5732 | 28.3788 | 24.9698 | 23.2965 | 17.8004 | 12.9381 | 10.9824 | 12.0579 | 15.8661 | 19.6828 | 24.2988 | 26.6015 | 28.7765 | 20.4708
5734 | 29.1257 | 25.5743 | 24.2292 | 19.1205 | 14.8797 | 13.0366 | 14.0472 | 17.5375 | 21.0599 | 24.5569 | 27.0027 | 28.1357 | 21.5255
5950 | 28.0129 | 24.5288 | 19.9915 | 13.8265 | 9.5051 | 7.5604 | 8.7333 | 12.2301 | 15.5101 | 20.4485 | 25.0066 | 27.5475 | 17.7418
5960 | 27.6021 | 24.1277 | 20.1763 | 13.9494 | 9.745 | 7.6824 | 8.8046 | 12.3605 | 15.8857 | 20.9103 | 25.1143 | 27.3004 | 17.8049
6000 | 30.0018 | 26.8245 | 21.3929 | 15.2271 | 10.9782 | 9.0526 | 10.0474 | 13.2432 | 17.027 | 23.2856 | 27.1233 | 30.2493 | 19.5377
6003 | 30.0018 | 26.8245 | 21.3929 | 15.2271 | 10.9782 | 9.0526 | 10.0474 | 13.2432 | 17.027 | 23.2856 | 27.1233 | 30.2493 | 19.5377
6004 | 29.9059 | 26.7943 | 21.4546 | 15.2612 | 10.9966 | 9.0092 | 9.9947 | 13.1884 | 16.902 | 23.0682 | 27.0338 | 30.1873 | 19.483
6005 | 30.0018 | 26.8245 | 21.3929 | 15.2271 | 10.9782 | 9.0526 | 10.0474 | 13.2432 | 17.027 | 23.2856 | 27.1233 | 30.2493 | 19.5377
6006 | 30.0018 | 26.8245 | 21.3929 | 15.2271 | 10.9782 | 9.0526 | 10.0474 | 13.2432 | 17.027 | 23.2856 | 27.1233 | 30.2493 | 19.5377
6007 | 30.0018 | 26.8245 | 21.3929 | 15.2271 | 10.9782 | 9.0526 | 10.0474 | 13.2432 | 17.027 | 23.2856 | 27.1233 | 30.2493 | 19.5377
6008 | 29.9755 | 26.7527 | 21.4425 | 15.2166 | 10.9035 | 9.1153 | 10.1036 | 13.3329 | 17.2594 | 23.4255 | 27.2941 | 30.2903 | 19.5927
6009 | 29.85 | 26.6682 | 21.4723 | 15.2419 | 10.8829 | 8.9442 | 10.0198 | 13.3244 | 17.3146 | 23.4131 | 27.242 | 30.2472 | 19.5517
6010 | 29.9755 | 26.7527 | 21.4425 | 15.2166 | 10.9035 | 9.1153 | 10.1036 | 13.3329 | 17.2594 | 23.4255 | 27.2941 | 30.2903 | 19.5927
6011 | 29.7601 | 26.5438 | 21.4366 | 15.1309 | 10.7081 | 8.9533 | 9.9916 | 13.4018 | 17.5002 | 23.6413 | 27.4314 | 30.2464 | 19.5621
6012 | 29.7601 | 26.5438 | 21.4366 | 15.1309 | 10.7081 | 8.9533 | 9.9916 | 13.4018 | 17.5002 | 23.6413 | 27.4314 | 30.2464 | 19.5621
6014 | 29.9755 | 26.7527 | 21.4425 | 15.2166 | 10.9035 | 9.1153 | 10.1036 | 13.3329 | 17.2594 | 23.4255 | 27.2941 | 30.2903 | 19.5927
6015 | 29.6774 | 26.5868 | 21.4333 | 15.1025 | 10.7214 | 9.0176 | 9.9871 | 13.3727 | 17.4201 | 23.6255 | 27.3797 | 30.2089 | 19.5444
6016 | 29.9212 | 26.7305 | 21.2869 | 15.2832 | 11.061 | 9.1294 | 10.1135 | 13.1984 | 16.9249 | 23.2309 | 27.0778 | 30.1972 | 19.5129
6017 | 29.9596 | 26.8519 | 21.3658 | 15.2046 | 11.036 | 9.1274 | 10.1576 | 13.2674 | 17.2366 | 23.4871 | 27.2839 | 30.2809 | 19.6049
6018 | 29.9596 | 26.8519 | 21.3658 | 15.2046 | 11.036 | 9.1274 | 10.1576 | 13.2674 | 17.2366 | 23.4871 | 27.2839 | 30.2809 | 19.6049
6019 | 29.7007 | 26.6176 | 21.3938 | 15.1392 | 10.8281 | 9.0641 | 10.1029 | 13.41 | 17.3723 | 23.625 | 27.4512 | 30.1832 | 19.574
6020 | 29.7657 | 26.6512 | 21.2723 | 15.2154 | 10.8828 | 9.1445 | 10.2332 | 13.4009 | 17.3472 | 23.6584 | 27.3948 | 30.1584 | 19.5937
6021 | 29.9596 | 26.8519 | 21.3658 | 15.2046 | 11.036 | 9.1274 | 10.1576 | 13.2674 | 17.2366 | 23.4871 | 27.2839 | 30.2809 | 19.6049
6022 | 29.829 | 26.6729 | 21.2779 | 15.3427 | 11.0657 | 9.166 | 10.1898 | 13.2563 | 17.2838 | 23.4962 | 27.2309 | 30.2521 | 19.5886
6023 | 29.829 | 26.6729 | 21.2779 | 15.3427 | 11.0657 | 9.166 | 10.1898 | 13.2563 | 17.2838 | 23.4962 | 27.2309 | 30.2521 | 19.5886
6024 | 29.829 | 26.6729 | 21.2779 | 15.3427 | 11.0657 | 9.166 | 10.1898 | 13.2563 | 17.2838 | 23.4962 | 27.2309 | 30.2521 | 19.5886
6025 | 29.8109 | 26.7551 | 21.2856 | 15.3089 | 10.978 | 9.233 | 10.2571 | 13.4317 | 17.4417 | 23.6892 | 27.3755 | 30.1517 | 19.6432
6026 | 29.7894 | 26.5468 | 21.2084 | 15.4372 | 11.0824 | 9.247 | 10.1666 | 13.2646 | 17.2782 | 23.4411 | 27.2347 | 30.2191 | 19.5763
6027 | 29.8538 | 26.8052 | 21.3623 | 15.4166 | 10.981 | 9.2127 | 10.2188 | 13.3977 | 17.4671 | 23.6547 | 27.338 | 30.1271 | 19.6529
6028 | 29.8538 | 26.8052 | 21.3623 | 15.4166 | 10.981 | 9.2127 | 10.2188 | 13.3977 | 17.4671 | 23.6547 | 27.338 | 30.1271 | 19.6529
6029 | 29.7007 | 26.6176 | 21.3938 | 15.1392 | 10.8281 | 9.0641 | 10.1029 | 13.41 | 17.3723 | 23.625 | 27.4512 | 30.1832 | 19.574
6030 | 29.6729 | 26.7406 | 21.4182 | 15.3061 | 10.815 | 9.1969 | 10.2221 | 13.4532 | 17.4275 | 23.7644 | 27.3253 | 30.0434 | 19.6155
6031 | 29.7279 | 26.4218 | 21.2842 | 15.5065 | 10.967 | 9.2639 | 10.1895 | 13.2662 | 17.2965 | 23.5044 | 27.1131 | 30.083 | 19.552
6032 | 29.7279 | 26.4218 | 21.2842 | 15.5065 | 10.967 | 9.2639 | 10.1895 | 13.2662 | 17.2965 | 23.5044 | 27.1131 | 30.083 | 19.552
6033 | 29.6711 | 26.5041 | 21.4322 | 15.4946 | 10.9038 | 9.3133 | 10.2045 | 13.3146 | 17.4592 | 23.5752 | 27.2366 | 30.1822 | 19.6076
6035 | 29.6505 | 26.6536 | 21.6006 | 15.4347 | 10.9202 | 9.2714 | 10.2535 | 13.3888 | 17.5714 | 23.7072 | 27.2374 | 30.0979 | 19.6489
6036 | 29.6835 | 26.7174 | 21.3887 | 15.4155 | 10.9308 | 9.2656 | 10.2291 | 13.326 | 17.4972 | 23.705 | 27.2233 | 30.0888 | 19.6226
6037 | 29.6781 | 26.3041 | 21.4274 | 15.4566 | 11.0317 | 9.3231 | 10.1509 | 13.2416 | 17.2336 | 23.249 | 27.0578 | 30.0249 | 19.5149
6041 | 29.5554 | 26.6383 | 21.6816 | 15.5373 | 11.0841 | 9.4196 | 10.4222 | 13.4942 | 17.6671 | 23.911 | 27.383 | 29.9522 | 19.7288
6042 | 29.5919 | 26.6315 | 21.6557 | 15.4894 | 11.0361 | 9.4739 | 10.4005 | 13.485 | 17.7563 | 23.9242 | 27.4394 | 29.9503 | 19.7362
6043 | 29.6237 | 26.6937 | 21.6534 | 15.5706 | 11.1964 | 9.5474 | 10.5609 | 13.6374 | 17.7417 | 24.0415 | 27.3222 | 29.9801 | 19.7974
6044 | 29.6412 | 26.4555 | 21.6528 | 15.9358 | 11.5602 | 9.8217 | 10.6363 | 13.5337 | 17.4726 | 23.9594 | 27.3163 | 30.0054 | 19.8326
6050 | 29.9212 | 26.7305 | 21.2869 | 15.2832 | 11.061 | 9.1294 | 10.1135 | 13.1984 | 16.9249 | 23.2309 | 27.0778 | 30.1972 | 19.5129
6051 | 29.9059 | 26.7943 | 21.4546 | 15.2612 | 10.9966 | 9.0092 | 9.9947 | 13.1884 | 16.902 | 23.0682 | 27.0338 | 30.1873 | 19.483
6052 | 29.8034 | 26.6569 | 21.2866 | 15.3721 | 11.0826 | 9.1002 | 10.0891 | 13.1392 | 16.7933 | 23.0596 | 26.9471 | 30.1204 | 19.4542
6053 | 29.8034 | 26.6569 | 21.2866 | 15.3721 | 11.0826 | 9.1002 | 10.0891 | 13.1392 | 16.7933 | 23.0596 | 26.9471 | 30.1204 | 19.4542
6054 | 29.7876 | 26.6715 | 21.3942 | 15.3404 | 11.0222 | 8.9626 | 9.9553 | 13.0693 | 16.6784 | 23.0112 | 26.8916 | 30.1135 | 19.4081
6055 | 29.744 | 26.5298 | 21.3641 | 15.3391 | 10.9255 | 8.9312 | 9.8218 | 12.8611 | 16.6582 | 22.937 | 26.6849 | 29.995 | 19.316
6056 | 29.6503 | 26.3784 | 21.3492 | 15.3485 | 10.8106 | 8.9162 | 9.797 | 12.7137 | 16.4421 | 22.8562 | 26.5623 | 29.8706 | 19.2246
6057 | 29.6716 | 26.5247 | 21.3586 | 15.2401 | 10.8146 | 8.8059 | 9.8171 | 12.8357 | 16.4936 | 22.7719 | 26.6118 | 29.7819 | 19.2273
6058 | 29.6716 | 26.5247 | 21.3586 | 15.2401 | 10.8146 | 8.8059 | 9.8171 | 12.8357 | 16.4936 | 22.7719 | 26.6118 | 29.7819 | 19.2273
6059 | 29.9212 | 26.7305 | 21.2869 | 15.2832 | 11.061 | 9.1294 | 10.1135 | 13.1984 | 16.9249 | 23.2309 | 27.0778 | 30.1972 | 19.5129
6060 | 29.9212 | 26.7305 | 21.2869 | 15.2832 | 11.061 | 9.1294 | 10.1135 | 13.1984 | 16.9249 | 23.2309 | 27.0778 | 30.1972 | 19.5129
6061 | 29.709 | 26.4331 | 21.1506 | 15.3926 | 11.063 | 9.1785 | 10.1141 | 13.1279 | 16.9701 | 23.1511 | 26.9928 | 30.115 | 19.4498
6062 | 29.8034 | 26.6569 | 21.2866 | 15.3721 | 11.0826 | 9.1002 | 10.0891 | 13.1392 | 16.7933 | 23.0596 | 26.9471 | 30.1204 | 19.4542
6063 | 29.7828 | 26.5129 | 21.2572 | 15.3715 | 11.0339 | 9.0236 | 10.036 | 13.0101 | 16.7216 | 23.037 | 26.9289 | 30.1116 | 19.4023
6064 | 29.709 | 26.4331 | 21.1506 | 15.3926 | 11.063 | 9.1785 | 10.1141 | 13.1279 | 16.9701 | 23.1511 | 26.9928 | 30.115 | 19.4498
6065 | 29.6759 | 26.2709 | 21.1154 | 15.4298 | 11.054 | 9.1745 | 10.1509 | 13.1549 | 17.0364 | 23.1914 | 27.0288 | 30.119 | 19.4502
6066 | 29.6899 | 26.2866 | 21.1397 | 15.4469 | 11.0497 | 9.1379 | 10.1141 | 13.1114 | 16.767 | 23.0548 | 26.9452 | 30.1416 | 19.4071
6067 | 29.6724 | 26.1575 | 21.2052 | 15.435 | 11.0254 | 9.1325 | 10.1023 | 13.1132 | 16.8159 | 23.0924 | 26.9994 | 30.064 | 19.4013
6068 | 29.7828 | 26.5129 | 21.2572 | 15.3715 | 11.0339 | 9.0236 | 10.036 | 13.0101 | 16.7216 | 23.037 | 26.9289 | 30.1116 | 19.4023
6069 | 29.6892 | 26.5716 | 21.3962 | 15.4632 | 10.9925 | 9.0885 | 9.889 | 12.9864 | 16.9021 | 23.204 | 26.7045 | 29.7578 | 19.3871
6070 | 29.6492 | 26.5035 | 21.4837 | 15.1476 | 10.6302 | 8.8366 | 9.602 | 12.6894 | 16.5059 | 22.6558 | 26.5726 | 29.7692 | 19.1705
6071 | 29.7202 | 26.5169 | 21.5147 | 15.2072 | 10.7286 | 8.8814 | 9.7127 | 12.7194 | 16.4745 | 22.8122 | 26.6745 | 29.877 | 19.2366
6072 | 29.6598 | 26.5827 | 21.5407 | 15.161 | 10.7225 | 8.9184 | 9.7314 | 12.8617 | 16.715 | 22.8487 | 26.7291 | 29.8854 | 19.2797
6073 | 29.6598 | 26.5827 | 21.5407 | 15.161 | 10.7225 | 8.9184 | 9.7314 | 12.8617 | 16.715 | 22.8487 | 26.7291 | 29.8854 | 19.2797
6074 | 29.5875 | 26.2179 | 21.4025 | 14.915 | 10.6476 | 8.9539 | 9.8778 | 12.8973 | 16.8945 | 22.891 | 26.7904 | 29.7212 | 19.2331
6076 | 29.6261 | 26.3344 | 21.4376 | 15.1547 | 10.6361 | 8.768 | 9.606 | 12.6364 | 16.4967 | 22.5696 | 26.5556 | 29.7828 | 19.1337
6077 | 29.7227 | 26.3249 | 21.308 | 15.4325 | 11.0581 | 9.1698 | 10.1608 | 13.2078 | 17.0525 | 23.2209 | 27.0431 | 30.0917 | 19.4827
6078 | 29.7842 | 26.4046 | 21.425 | 15.4703 | 11.172 | 9.2312 | 10.1672 | 13.2666 | 17.0397 | 23.2001 | 27.0706 | 30.1032 | 19.5279
6079 | 29.6146 | 26.2416 | 21.2982 | 15.4054 | 11.0936 | 9.1375 | 10.1081 | 13.1522 | 16.8781 | 23.1086 | 27.0064 | 29.9358 | 19.415
6081 | 29.7916 | 26.5442 | 21.5055 | 15.2031 | 10.7876 | 9.0507 | 9.8359 | 12.7913 | 16.6275 | 22.9059 | 26.8506 | 30.0006 | 19.3245
6082 | 29.7816 | 26.541 | 21.4906 | 15.2005 | 10.8167 | 9.1011 | 9.8465 | 12.7522 | 16.7431 | 23.0161 | 26.8771 | 29.9624 | 19.3441
6083 | 29.5732 | 26.1022 | 21.3137 | 15.4016 | 10.9267 | 9.2877 | 9.9098 | 12.8739 | 16.862 | 23.1727 | 27.1346 | 29.9123 | 19.3725
6084 | 29.776 | 26.4564 | 21.5614 | 15.5198 | 11.0304 | 9.1755 | 10.0762 | 13.1534 | 17.0575 | 23.2666 | 26.8597 | 29.8661 | 19.4833
6090 | 29.6899 | 26.2866 | 21.1397 | 15.4469 | 11.0497 | 9.1379 | 10.1141 | 13.1114 | 16.767 | 23.0548 | 26.9452 | 30.1416 | 19.4071
6100 | 29.9059 | 26.7943 | 21.4546 | 15.2612 | 10.9966 | 9.0092 | 9.9947 | 13.1884 | 16.902 | 23.0682 | 27.0338 | 30.1873 | 19.483
6101 | 29.9764 | 26.8067 | 21.3986 | 15.2788 | 11.0129 | 8.9722 | 9.9717 | 13.1288 | 16.9071 | 23.0097 | 26.9218 | 30.1554 | 19.4617
6102 | 29.9764 | 26.8067 | 21.3986 | 15.2788 | 11.0129 | 8.9722 | 9.9717 | 13.1288 | 16.9071 | 23.0097 | 26.9218 | 30.1554 | 19.4617
6103 | 29.9059 | 26.7943 | 21.4546 | 15.2612 | 10.9966 | 9.0092 | 9.9947 | 13.1884 | 16.902 | 23.0682 | 27.0338 | 30.1873 | 19.483
6104 | 29.8628 | 26.7531 | 21.3825 | 15.2677 | 10.9556 | 8.9113 | 9.9166 | 13.0353 | 16.7467 | 22.9432 | 26.8322 | 30.0019 | 19.3841
6105 | 29.8628 | 26.7531 | 21.3825 | 15.2677 | 10.9556 | 8.9113 | 9.9166 | 13.0353 | 16.7467 | 22.9432 | 26.8322 | 30.0019 | 19.3841
6106 | 29.8449 | 26.7083 | 21.3327 | 15.2258 | 10.8976 | 8.8892 | 9.8626 | 12.9392 | 16.6903 | 22.8882 | 26.6433 | 29.9359 | 19.3215
6107 | 29.8449 | 26.7083 | 21.3327 | 15.2258 | 10.8976 | 8.8892 | 9.8626 | 12.9392 | 16.6903 | 22.8882 | 26.6433 | 29.9359 | 19.3215
6108 | 29.7587 | 26.7109 | 21.334 | 15.2008 | 10.8231 | 8.8335 | 9.761 | 12.8971 | 16.613 | 22.8401 | 26.5683 | 29.8931 | 19.2695
6109 | 29.5869 | 26.4672 | 21.3402 | 15.1292 | 10.6267 | 8.6799 | 9.6053 | 12.7075 | 16.3874 | 22.6683 | 26.2317 | 29.6615 | 19.091
6110 | 29.5151 | 26.4175 | 21.2579 | 15.0514 | 10.5625 | 8.6466 | 9.5438 | 12.6002 | 16.3069 | 22.52 | 26.0638 | 29.561 | 19.0039
6111 | 29.6901 | 26.3522 | 21.3083 | 14.908 | 10.5773 | 8.6472 | 9.5536 | 12.5708 | 16.2437 | 22.4131 | 26.3518 | 29.6621 | 19.0232
6112 | 29.5146 | 26.4603 | 21.2049 | 14.9947 | 10.586 | 8.5797 | 9.5241 | 12.4893 | 16.2082 | 22.5376 | 26.1267 | 29.4392 | 18.9721
6121 | 29.7302 | 26.6324 | 21.1636 | 15.116 | 10.8987 | 8.8122 | 9.7004 | 12.7918 | 16.4067 | 22.8657 | 26.7231 | 29.9968 | 19.2365
6122 | 29.5112 | 26.2761 | 21.2108 | 14.9417 | 10.5925 | 8.4802 | 9.4269 | 12.3652 | 16.1855 | 22.3206 | 26.1529 | 29.5621 | 18.9188
6123 | 29.7209 | 26.8007 | 21.1834 | 15.0119 | 10.698 | 8.5402 | 9.3669 | 12.4994 | 16.3153 | 22.5542 | 26.3751 | 29.6552 | 19.0601
6124 | 29.6831 | 26.3798 | 21.1974 | 14.8085 | 10.5037 | 8.5667 | 9.4825 | 12.3343 | 16.1367 | 22.1752 | 26.1354 | 29.5293 | 18.911
6125 | 29.664 | 26.7424 | 21.171 | 15.0518 | 10.6785 | 8.4749 | 9.2777 | 12.4477 | 16.3394 | 22.4508 | 26.3851 | 29.6008 | 19.0237
6126 | 29.3904 | 26.2253 | 21.1449 | 14.9204 | 10.4898 | 8.3237 | 9.1793 | 12.1903 | 15.9727 | 22.1446 | 26.0328 | 29.3608 | 18.7812
6147 | 29.7587 | 26.7109 | 21.334 | 15.2008 | 10.8231 | 8.8335 | 9.761 | 12.8971 | 16.613 | 22.8401 | 26.5683 | 29.8931 | 19.2695
6148 | 29.9275 | 26.8207 | 21.3448 | 15.2436 | 10.969 | 8.932 | 9.913 | 13.0167 | 16.8687 | 22.9851 | 26.8748 | 30.1334 | 19.4191
6149 | 29.9108 | 26.5707 | 21.2596 | 15.1835 | 10.95 | 8.9318 | 9.969 | 13.1486 | 17.009 | 23.1283 | 27.0825 | 30.182 | 19.4438
6150 | 29.9108 | 26.5707 | 21.2596 | 15.1835 | 10.95 | 8.9318 | 9.969 | 13.1486 | 17.009 | 23.1283 | 27.0825 | 30.182 | 19.4438
6151 | 29.894 | 26.6665 | 21.4544 | 15.1524 | 10.9409 | 8.9584 | 10.0207 | 13.2122 | 17.0897 | 23.1993 | 27.1504 | 30.1699 | 19.4924
6152 | 29.9764 | 26.8067 | 21.3986 | 15.2788 | 11.0129 | 8.9722 | 9.9717 | 13.1288 | 16.9071 | 23.0097 | 26.9218 | 30.1554 | 19.4617
6153 | 29.894 | 26.6665 | 21.4544 | 15.1524 | 10.9409 | 8.9584 | 10.0207 | 13.2122 | 17.0897 | 23.1993 | 27.1504 | 30.1699 | 19.4924
6154 | 29.9108 | 26.5707 | 21.2596 | 15.1835 | 10.95 | 8.9318 | 9.969 | 13.1486 | 17.009 | 23.1283 | 27.0825 | 30.182 | 19.4438
6155 | 29.8687 | 26.8128 | 21.2193 | 15.2125 | 10.9611 | 8.9263 | 9.9189 | 13.0486 | 16.689 | 23.0104 | 26.7643 | 29.9872 | 19.3683
6156 | 29.6619 | 26.4437 | 21.2035 | 15.2609 | 10.8982 | 8.8655 | 9.9462 | 13.1911 | 17.1513 | 23.2194 | 27.1888 | 30.1408 | 19.4309
6157 | 29.6619 | 26.4437 | 21.2035 | 15.2609 | 10.8982 | 8.8655 | 9.9462 | 13.1911 | 17.1513 | 23.2194 | 27.1888 | 30.1408 | 19.4309
6158 | 29.6911 | 26.6387 | 21.4243 | 15.2795 | 10.8188 | 8.8586 | 9.982 | 13.3096 | 17.4033 | 23.4827 | 27.3623 | 30.212 | 19.5386
6159 | 29.6911 | 26.6387 | 21.4243 | 15.2795 | 10.8188 | 8.8586 | 9.982 | 13.3096 | 17.4033 | 23.4827 | 27.3623 | 30.212 | 19.5386
6160 | 29.6911 | 26.6387 | 21.4243 | 15.2795 | 10.8188 | 8.8586 | 9.982 | 13.3096 | 17.4033 | 23.4827 | 27.3623 | 30.212 | 19.5386
6161 | 29.7601 | 26.5438 | 21.4366 | 15.1309 | 10.7081 | 8.9533 | 9.9916 | 13.4018 | 17.5002 | 23.6413 | 27.4314 | 30.2464 | 19.5621
6162 | 29.6911 | 26.6387 | 21.4243 | 15.2795 | 10.8188 | 8.8586 | 9.982 | 13.3096 | 17.4033 | 23.4827 | 27.3623 | 30.212 | 19.5386
6163 | 29.8559 | 26.7043 | 21.0755 | 15.2549 | 10.9651 | 8.954 | 9.9913 | 13.103 | 17.0495 | 23.1876 | 27.1326 | 30.1388 | 19.451
6164 | 29.9004 | 26.7564 | 21.15 | 15.1743 | 10.9754 | 8.9714 | 9.9017 | 13.085 | 16.8835 | 23.1986 | 26.9488 | 30.2089 | 19.4295
6165 | 29.9282 | 26.8025 | 21.2444 | 15.1093 | 10.9117 | 8.9291 | 9.9622 | 13.1225 | 17.1145 | 23.2506 | 27.1465 | 30.23 | 19.4793
6166 | 30.0303 | 26.9176 | 21.2495 | 15.1603 | 10.9583 | 8.9549 | 9.9924 | 13.1658 | 17.1448 | 23.2932 | 27.1619 | 30.2937 | 19.5269
6167 | 29.8006 | 26.608 | 21.223 | 15.1537 | 10.9442 | 8.8811 | 9.8714 | 13.0267 | 16.8381 | 23.0964 | 26.9568 | 30.1989 | 19.3832
6168 | 29.8243 | 26.6858 | 21.076 | 15.1727 | 10.8149 | 8.8138 | 9.8616 | 13.0275 | 16.9135 | 23.2521 | 27.3044 | 30.2503 | 19.4164
6169 | 29.8243 | 26.6858 | 21.076 | 15.1727 | 10.8149 | 8.8138 | 9.8616 | 13.0275 | 16.9135 | 23.2521 | 27.3044 | 30.2503 | 19.4164
6170 | 29.8097 | 26.5328 | 21.1838 | 15.193 | 10.9348 | 8.9204 | 9.7873 | 12.904 | 16.6297 | 22.9925 | 26.9388 | 30.2199 | 19.3372
6171 | 29.907 | 26.7619 | 21.1582 | 15.1547 | 10.9213 | 8.6939 | 9.615 | 12.7896 | 16.4423 | 22.8935 | 26.8975 | 30.1744 | 19.2841
6172 | 29.8341 | 26.8049 | 21.1715 | 15.0473 | 10.7389 | 8.7957 | 9.8917 | 13.089 | 16.8306 | 23.168 | 27.2846 | 30.1966 | 19.4044
6173 | 29.8746 | 26.7914 | 21.282 | 15.0461 | 10.6901 | 8.7082 | 9.8231 | 13.1464 | 16.777 | 23.1428 | 27.2762 | 30.1295 | 19.3906
6174 | 29.8745 | 26.772 | 21.3733 | 14.9747 | 10.6337 | 8.6635 | 9.6406 | 13.0608 | 16.7461 | 23.1561 | 27.3965 | 30.2497 | 19.3785
6175 | 29.8745 | 26.772 | 21.3733 | 14.9747 | 10.6337 | 8.6635 | 9.6406 | 13.0608 | 16.7461 | 23.1561 | 27.3965 | 30.2497 | 19.3785
6176 | 29.8923 | 26.871 | 21.2304 | 15.1433 | 10.8432 | 8.7122 | 9.6638 | 12.9203 | 16.5867 | 23.041 | 27.2317 | 30.1769 | 19.3594
6180 | 29.8719 | 26.7067 | 21.3511 | 15.0567 | 10.7064 | 8.5957 | 9.5925 | 12.9795 | 16.7384 | 23.0395 | 27.4168 | 30.2393 | 19.3579
6181 | 29.9331 | 26.6985 | 21.1755 | 15.1436 | 10.7797 | 8.6196 | 9.6089 | 12.8553 | 16.6101 | 22.8818 | 27.1994 | 30.2471 | 19.3127
6182 | 29.8151 | 26.6948 | 21.1294 | 15.0843 | 10.7992 | 8.5825 | 9.5783 | 12.7699 | 16.411 | 22.8616 | 26.9649 | 30.1125 | 19.2336
6207 | 29.81 | 26.7584 | 21.1277 | 14.9837 | 10.6692 | 8.3496 | 9.3853 | 12.5408 | 16.1846 | 22.6608 | 26.684 | 29.8651 | 19.0849
6208 | 29.7534 | 26.6314 | 20.9957 | 15.0086 | 10.6015 | 8.2993 | 9.2665 | 12.5144 | 16.2949 | 22.43 | 26.619 | 29.5185 | 18.9944
6209 | 29.9026 | 26.6928 | 21.1394 | 15.1066 | 10.8106 | 8.5839 | 9.5873 | 12.7863 | 16.4906 | 22.7993 | 27.1996 | 30.1159 | 19.2679
6210 | 29.8719 | 26.7067 | 21.3511 | 15.0567 | 10.7064 | 8.5957 | 9.5925 | 12.9795 | 16.7384 | 23.0395 | 27.4168 | 30.2393 | 19.3579
6211 | 29.7734 | 26.6471 | 21.2709 | 15.0926 | 10.6087 | 8.2945 | 9.5322 | 12.6912 | 16.1643 | 22.5607 | 27.1158 | 29.7858 | 19.1281
6213 | 29.5196 | 26.2091 | 20.9773 | 14.7319 | 10.3699 | 8.4018 | 9.2527 | 12.2067 | 15.8734 | 21.9749 | 26.18 | 29.5236 | 18.7684
6214 | 29.504 | 26.4409 | 20.9727 | 14.813 | 10.3173 | 8.0889 | 9.0494 | 12.197 | 16.0528 | 22.085 | 26.0944 | 29.3268 | 18.7452
6215 | 29.3963 | 26.5629 | 21.0347 | 14.7404 | 10.2845 | 7.9387 | 8.8951 | 12.0813 | 15.937 | 22.0524 | 25.9749 | 29.1605 | 18.6716
6218 | 29.3697 | 26.397 | 20.9704 | 14.5585 | 10.1145 | 7.9308 | 8.9298 | 11.7455 | 15.7535 | 21.7348 | 25.8913 | 29.1824 | 18.5482
6220 | 29.1469 | 26.0984 | 20.7806 | 14.3997 | 10.0736 | 7.8986 | 8.7587 | 11.7629 | 15.6114 | 21.5739 | 25.9463 | 29.0268 | 18.4231
6221 | 29.4456 | 26.4941 | 20.8502 | 14.3795 | 10.1773 | 7.9512 | 8.9044 | 11.976 | 15.6409 | 21.6708 | 26.349 | 29.4789 | 18.6098
6224 | 29.4088 | 26.4378 | 20.8635 | 14.3912 | 10.0623 | 7.8292 | 8.7508 | 11.9759 | 15.561 | 21.6169 | 26.3272 | 29.4974 | 18.5602
6225 | 29.213 | 25.5868 | 20.4871 | 14.137 | 9.9277 | 8.1086 | 8.9973 | 11.7011 | 15.3434 | 21.2112 | 25.3395 | 28.8905 | 18.2453
6226 | 29.2807 | 26.2541 | 20.7669 | 14.2652 | 9.9222 | 7.7489 | 8.7186 | 11.8392 | 15.5348 | 21.4194 | 26.0959 | 29.3033 | 18.4291
6227 | 29.5936 | 26.5129 | 20.7192 | 14.2967 | 10.1454 | 7.8778 | 8.7875 | 12.0338 | 15.5848 | 21.5995 | 26.5124 | 29.6201 | 18.607
6229 | 29.4685 | 26.3297 | 20.7174 | 14.1939 | 10.0371 | 7.8044 | 8.7212 | 11.923 | 15.4824 | 21.4075 | 26.2845 | 29.4458 | 18.4846
6230 | 29.7695 | 26.2053 | 20.496 | 14.3556 | 10.2908 | 8.2324 | 9.1363 | 12.2667 | 15.4979 | 21.6273 | 26.6493 | 29.737 | 18.6887
6232 | 29.5544 | 26.2434 | 20.5267 | 14.2639 | 10.2358 | 8.0777 | 8.9207 | 12.1711 | 15.545 | 21.7891 | 26.7955 | 29.6881 | 18.651
6233 | 29.5133 | 26.2535 | 20.6421 | 14.239 | 10.1855 | 8.1735 | 8.9553 | 12.1864 | 15.6955 | 21.8436 | 26.8776 | 29.6702 | 18.6863
6236 | 29.1598 | 25.5583 | 20.418 | 13.9428 | 9.7747 | 7.835 | 8.6218 | 11.7143 | 15.2747 | 20.9374 | 25.5241 | 28.875 | 18.1363
6237 | 29.7464 | 26.133 | 20.4044 | 14.0722 | 9.9402 | 7.8198 | 8.7964 | 12.1979 | 15.6262 | 21.0975 | 26.2622 | 29.3435 | 18.4533
6239 | 29.1743 | 25.5187 | 20.0943 | 13.7678 | 9.5214 | 7.7958 | 8.701 | 11.7041 | 15.1194 | 20.6933 | 25.2786 | 28.7462 | 18.0096
6240 | 29.1683 | 25.4062 | 20.1191 | 13.8323 | 9.7728 | 7.9397 | 8.7794 | 11.6234 | 14.9836 | 20.7548 | 25.2696 | 28.8618 | 18.0426
6244 | 28.536 | 24.681 | 19.8452 | 13.6757 | 9.7684 | 7.9107 | 8.811 | 11.4771 | 15.0431 | 20.5561 | 25.2188 | 28.2539 | 17.8148
6251 | 28.8434 | 25.1014 | 19.909 | 13.6152 | 9.4527 | 7.6583 | 8.5264 | 11.5021 | 14.9765 | 20.3213 | 25.0595 | 28.3339 | 17.775
6253 | 28.8013 | 25.0563 | 19.7519 | 13.4585 | 9.4936 | 7.6402 | 8.5903 | 11.5547 | 14.7953 | 20.3579 | 24.9278 | 28.1261 | 17.7128
6254 | 28.6716 | 24.8747 | 19.5297 | 13.429 | 9.4808 | 7.582 | 8.5641 | 11.4197 | 14.8324 | 20.149 | 24.844 | 27.9607 | 17.6115
6255 | 28.2686 | 24.4009 | 19.4514 | 13.1606 | 9.3306 | 7.4283 | 8.5795 | 11.3914 | 14.8709 | 20.3406 | 24.7317 | 27.7628 | 17.4764
6256 | 28.2926 | 24.4726 | 19.3678 | 13.1462 | 9.3146 | 7.3939 | 8.5019 | 11.264 | 14.7992 | 20.0893 | 24.6548 | 27.4637 | 17.3967
6258 | 27.0339 | 23.3036 | 18.4997 | 12.7187 | 9.1354 | 7.3073 | 8.5364 | 11.3508 | 14.5532 | 19.6725 | 23.6751 | 26.2738 | 16.8384
6260 | 26.4602 | 23.0539 | 18.0216 | 12.4913 | 9.079 | 7.1542 | 8.2556 | 11.1773 | 14.2151 | 19.2783 | 23.3899 | 25.5883 | 16.5137
6262 | 25.0184 | 21.9307 | 17.1751 | 12.2048 | 8.8016 | 6.9901 | 8.0766 | 10.8365 | 13.8274 | 19.0346 | 22.7056 | 24.6409 | 15.9368
6271 | 29.757 | 25.9894 | 20.3065 | 14.2417 | 10.2098 | 8.0951 | 9.0024 | 12.1923 | 15.533 | 21.2646 | 26.677 | 29.4469 | 18.5596
6275 | 27.6286 | 24.0803 | 18.7547 | 12.8454 | 9.2343 | 7.3608 | 8.4091 | 11.2654 | 14.3383 | 19.4955 | 24.1323 | 26.7878 | 17.0277
6280 | 29.5529 | 25.9008 | 20.2188 | 13.9299 | 10.0288 | 7.8657 | 8.7931 | 12.1066 | 15.2177 | 20.7815 | 25.9529 | 28.9514 | 18.275
6281 | 29.8832 | 26.5446 | 20.7026 | 14.291 | 10.1477 | 7.8459 | 8.7613 | 12.2427 | 15.9955 | 21.4571 | 26.5549 | 29.1583 | 18.6321
6282 | 29.4875 | 26.1424 | 19.9692 | 13.9839 | 9.862 | 7.6186 | 8.6072 | 11.9793 | 15.4195 | 20.8967 | 25.8577 | 28.7235 | 18.2123
6284 | 28.3332 | 24.7314 | 19.4101 | 13.2417 | 9.3673 | 7.4887 | 8.366 | 11.4214 | 14.7155 | 20.0262 | 24.6979 | 27.5439 | 17.4453
6285 | 28.5039 | 24.9155 | 19.3012 | 13.2594 | 9.3386 | 7.41 | 8.3434 | 11.4607 | 14.8773 | 20.094 | 24.8452 | 27.8123 | 17.5135
6286 | 27.8955 | 24.6746 | 18.7655 | 12.9632 | 9.174 | 7.1065 | 8.2546 | 11.4037 | 14.6481 | 20.1079 | 24.7669 | 27.4051 | 17.2638
6288 | 27.4665 | 24.4185 | 18.5912 | 12.7816 | 9.1224 | 7.0739 | 8.2574 | 11.3502 | 14.6351 | 20.0489 | 24.7433 | 27.2271 | 17.143
6290 | 27.5186 | 24.2096 | 18.65 | 12.8299 | 9.2223 | 7.2303 | 8.3491 | 11.2684 | 14.3577 | 19.7593 | 24.3587 | 26.791 | 17.0454
6302 | 29.5258 | 25.9362 | 21.3993 | 15.5174 | 11.2869 | 9.5653 | 10.2699 | 13.0824 | 17.2657 | 23.6899 | 27.065 | 29.6655 | 19.5224
6304 | 29.3981 | 25.8795 | 20.9729 | 15.1886 | 11.1897 | 9.4306 | 10.1199 | 12.9013 | 17.0592 | 23.4064 | 27.2147 | 29.5918 | 19.3627
6306 | 29.1669 | 25.6924 | 20.9631 | 15.2547 | 11.0748 | 9.3165 | 10.0925 | 13.0596 | 16.9796 | 23.3132 | 26.988 | 29.3547 | 19.2713
6308 | 29.1889 | 25.5753 | 21.0442 | 15.1087 | 10.91 | 9.1594 | 9.8352 | 12.701 | 16.5508 | 22.9734 | 26.7552 | 29.4819 | 19.107
6309 | 29.1628 | 25.5641 | 20.9493 | 15.0859 | 10.7995 | 9.1461 | 9.7643 | 12.7326 | 16.4207 | 22.9206 | 26.6138 | 29.2398 | 19.0333
6311 | 28.979 | 25.3552 | 20.7291 | 14.8787 | 10.6384 | 9.0446 | 9.6634 | 12.4839 | 16.2677 | 22.6704 | 26.5189 | 29.1 | 18.8608
6312 | 28.7796 | 25.3383 | 20.7336 | 15.123 | 10.7288 | 9.207 | 9.7837 | 12.5564 | 16.6004 | 23.1028 | 26.47 | 29.0602 | 18.957
6313 | 28.8373 | 25.2108 | 20.5707 | 14.8471 | 10.5386 | 9.0654 | 9.7592 | 12.3927 | 16.3599 | 22.5513 | 26.1779 | 28.7605 | 18.7559
6315 | 28.6681 | 24.9396 | 20.4184 | 14.7439 | 10.3897 | 8.8829 | 9.4765 | 12.2916 | 15.9592 | 22.2418 | 25.9339 | 28.6434 | 18.5491
6316 | 28.3053 | 24.8251 | 20.2235 | 14.406 | 10.2253 | 8.6387 | 9.5398 | 12.0156 | 15.6962 | 21.6188 | 25.6434 | 28.3044 | 18.2868
6317 | 28.4773 | 24.853 | 20.1492 | 14.5135 | 10.1213 | 8.6346 | 9.4034 | 12.0658 | 15.7672 | 21.9755 | 25.506 | 28.2591 | 18.3105
6318 | 28.2076 | 24.8098 | 20.0954 | 14.185 | 9.9718 | 8.4721 | 9.2791 | 11.7592 | 15.3919 | 21.3801 | 25.1466 | 28.1096 | 18.0674
6320 | 27.9784 | 24.4869 | 19.6985 | 13.9583 | 9.8781 | 8.3548 | 9.2481 | 11.7994 | 15.281 | 20.8815 | 24.8311 | 27.9068 | 17.8586
6321 | 27.1727 | 23.6769 | 19.0187 | 13.423 | 9.5859 | 8.0473 | 9.0239 | 11.6594 | 15.2263 | 20.3146 | 24.2486 | 27.1478 | 17.3788
6322 | 27.1326 | 23.6559 | 18.8918 | 13.4035 | 9.6565 | 8.195 | 9.1483 | 11.9072 | 15.2795 | 20.4931 | 24.2378 | 26.9448 | 17.4122
6323 | 26.6345 | 22.8537 | 18.3446 | 13.0816 | 9.4115 | 7.8407 | 8.8874 | 11.4022 | 15.0915 | 19.8682 | 23.8488 | 26.4553 | 16.9767
6324 | 25.9518 | 22.0711 | 17.5976 | 12.8849 | 9.28 | 7.8313 | 8.9911 | 11.4186 | 14.7178 | 19.5797 | 23.3135 | 25.705 | 16.6119
6326 | 25.2918 | 21.4105 | 16.9371 | 12.4464 | 9.0698 | 7.7172 | 8.8117 | 11.3707 | 14.5963 | 18.941 | 22.8625 | 25.1719 | 16.2189
6327 | 24.8189 | 21.2061 | 16.6045 | 12.2339 | 8.8833 | 7.4954 | 8.5241 | 11.3484 | 14.513 | 18.6308 | 22.725 | 24.63 | 15.9678
6328 | 24.7073 | 21.1509 | 17.0255 | 12.4708 | 9.0339 | 7.9937 | 9.0378 | 11.7149 | 15.5032 | 19.4199 | 22.9748 | 24.2848 | 16.2765
6330 | 24.4272 | 20.9276 | 16.4925 | 12.3491 | 8.7995 | 7.4756 | 8.6053 | 11.2932 | 14.4397 | 18.6256 | 22.3303 | 23.977 | 15.8119
6333 | 24.5042 | 21.131 | 16.7464 | 12.2326 | 8.8147 | 7.255 | 8.3209 | 10.9171 | 14.0131 | 18.6054 | 22.4449 | 24.3751 | 15.78
6335 | 27.696 | 24.4418 | 19.6955 | 14.1241 | 9.9444 | 8.562 | 9.3366 | 11.9397 | 15.6223 | 21.2167 | 24.674 | 27.8489 | 17.9252
6336 | 27.3462 | 23.8575 | 19.2148 | 13.9378 | 9.793 | 8.6973 | 9.42 | 12.1724 | 15.7919 | 21.2025 | 24.4385 | 27.224 | 17.758
6337 | 26.4477 | 23.0848 | 18.6674 | 13.679 | 9.8319 | 8.8238 | 9.5186 | 12.4704 | 16.2676 | 21.2062 | 24.0235 | 26.2716 | 17.5244
6338 | 25.5647 | 22.0856 | 17.7489 | 13.1613 | 9.4883 | 8.4857 | 9.2964 | 12.0931 | 15.8682 | 20.3171 | 23.3718 | 25.5428 | 16.9187
6341 | 28.3755 | 24.8099 | 20.1801 | 14.678 | 10.092 | 8.7143 | 9.5024 | 12.2106 | 16.0371 | 22.0111 | 25.4627 | 27.8816 | 18.3296
6343 | 27.9681 | 24.5297 | 19.7204 | 14.422 | 10.0031 | 8.8771 | 9.4717 | 12.5012 | 16.5177 | 22.2548 | 25.0586 | 27.3983 | 18.2269
6346 | 25.6783 | 22.1144 | 18.2689 | 13.7949 | 9.7883 | 9.0525 | 9.5635 | 12.5535 | 16.0583 | 21.1005 | 23.5847 | 25.9372 | 17.2913
6348 | 26.5182 | 23.09 | 18.9664 | 13.9366 | 9.9856 | 9.1791 | 9.6072 | 12.7369 | 16.6194 | 21.6671 | 24.3269 | 26.4654 | 17.7582
6350 | 28.6063 | 24.9601 | 20.3569 | 14.9371 | 10.304 | 9.0225 | 9.724 | 12.2129 | 16.1227 | 22.3472 | 25.7181 | 28.3497 | 18.5551
6352 | 28.6248 | 25.1628 | 20.3144 | 14.8957 | 10.295 | 9.0772 | 9.6267 | 12.3377 | 16.3273 | 22.5824 | 25.7544 | 28.4036 | 18.6168
6353 | 28.4248 | 24.9034 | 20.4161 | 14.9328 | 10.486 | 9.1944 | 9.7451 | 12.7915 | 16.8014 | 22.9495 | 25.9177 | 28.4927 | 18.7546
6355 | 27.9281 | 24.4772 | 19.9902 | 14.6562 | 10.1874 | 9.1117 | 9.6407 | 12.9533 | 17.0274 | 22.667 | 25.3476 | 28.022 | 18.5007
6358 | 28.4543 | 24.8305 | 20.6069 | 15.3225 | 10.7923 | 9.2896 | 9.8555 | 13.1696 | 17.3396 | 23.494 | 26.761 | 28.8646 | 19.065
6359 | 28.226 | 24.7459 | 20.5586 | 15.01 | 10.5038 | 9.3511 | 9.8258 | 13.2177 | 17.3424 | 22.9937 | 26.2372 | 28.6335 | 18.8871
6365 | 28.6659 | 25.2504 | 20.7266 | 15.3031 | 10.7499 | 9.3174 | 9.7439 | 12.7695 | 16.9321 | 23.2833 | 26.5508 | 28.9303 | 19.0186
6367 | 28.9483 | 25.6217 | 20.8811 | 15.4541 | 10.9439 | 9.4798 | 9.9115 | 12.954 | 17.1168 | 23.4963 | 26.5888 | 29.0604 | 19.2047
6368 | 28.9786 | 25.7491 | 21.2951 | 15.6337 | 11.1036 | 9.6686 | 10.2386 | 13.4112 | 17.4461 | 23.6005 | 26.9589 | 29.0296 | 19.4261
6369 | 28.5852 | 25.0239 | 21.0552 | 15.6353 | 10.9296 | 9.4933 | 9.9468 | 13.3212 | 17.6485 | 23.4196 | 26.8055 | 28.782 | 19.2205
6370 | 29.0079 | 25.4503 | 20.8567 | 15.2028 | 10.8335 | 9.2304 | 9.8779 | 12.7837 | 16.7795 | 23.1309 | 26.6194 | 29.0734 | 19.0705
6373 | 28.7659 | 25.4882 | 21.1321 | 15.4631 | 11.0713 | 9.4882 | 10.1026 | 13.2211 | 17.1625 | 23.7014 | 27.024 | 28.8106 | 19.2859
6375 | 29.0449 | 25.6409 | 21.0885 | 15.5098 | 11.1186 | 9.6361 | 10.1183 | 13.2123 | 17.4119 | 23.5073 | 26.7518 | 29.1837 | 19.352
6383 | 29.178 | 25.6968 | 21.2986 | 15.6743 | 11.285 | 9.7157 | 10.4526 | 13.4835 | 17.5414 | 23.6588 | 26.8878 | 29.0579 | 19.4942
6386 | 29.1035 | 25.6927 | 21.2524 | 15.8407 | 11.2594 | 9.853 | 10.3086 | 13.5119 | 17.5402 | 23.574 | 26.9102 | 29.2297 | 19.5064
6390 | 29.1901 | 25.5052 | 20.5461 | 14.4707 | 10.4008 | 8.6173 | 9.4738 | 12.0516 | 15.8024 | 21.8373 | 26.281 | 29.2903 | 18.6222
6391 | 29.0904 | 25.5016 | 20.6301 | 14.5294 | 10.4142 | 8.6427 | 9.4442 | 11.9436 | 15.849 | 21.9971 | 26.4483 | 29.2282 | 18.6432
6392 | 28.9103 | 25.2789 | 20.2618 | 14.1155 | 10.1112 | 8.3654 | 9.1098 | 11.8094 | 15.335 | 21.354 | 25.7403 | 28.9124 | 18.2753
6393 | 28.7766 | 25.0492 | 20.1745 | 14.3984 | 10.1563 | 8.4872 | 9.3579 | 11.9056 | 15.5161 | 21.5231 | 25.7163 | 28.7527 | 18.3178
6394 | 28.6163 | 24.8633 | 20.0218 | 14.1166 | 9.9205 | 8.1996 | 9.0611 | 11.6335 | 15.1716 | 20.9881 | 25.3531 | 28.5638 | 18.0424
6395 | 28.3469 | 24.4476 | 19.8144 | 13.9458 | 9.8238 | 7.9364 | 8.9267 | 11.6257 | 15.0858 | 20.7955 | 25.174 | 28.2536 | 17.848
6396 | 27.2061 | 23.5008 | 18.7225 | 13.1758 | 9.443 | 7.6156 | 8.7263 | 11.3896 | 14.7674 | 19.9174 | 24.1567 | 26.9577 | 17.1316
6397 | 26.1471 | 22.4203 | 17.8022 | 12.7141 | 9.0559 | 7.5075 | 8.6018 | 11.4674 | 14.5221 | 19.2383 | 23.2654 | 25.8025 | 16.5454
6398 | 24.8107 | 21.2522 | 16.8652 | 12.2856 | 8.8773 | 7.1688 | 8.2939 | 10.9542 | 13.9494 | 18.884 | 22.5481 | 24.468 | 15.8631
6401 | 29.2405 | 25.9467 | 21.4584 | 15.8838 | 11.4236 | 9.8323 | 10.4977 | 13.3756 | 17.3717 | 23.8728 | 27.2176 | 29.6897 | 19.6509
6403 | 29.0224 | 25.8393 | 21.4258 | 15.8187 | 11.4535 | 9.8383 | 10.6014 | 13.5607 | 17.5016 | 23.9675 | 27.3839 | 29.4393 | 19.6544
6405 | 29.1174 | 25.7236 | 21.4965 | 15.8184 | 11.4624 | 9.8953 | 10.7118 | 13.7709 | 17.7846 | 24.1747 | 27.3057 | 29.2141 | 19.7063
6407 | 28.9469 | 25.8799 | 21.5827 | 16.1163 | 11.5044 | 9.902 | 10.6084 | 13.6813 | 17.8655 | 23.941 | 27.2084 | 28.9434 | 19.6817
6409 | 28.9503 | 25.8089 | 21.6476 | 16.1506 | 11.482 | 9.8883 | 10.6154 | 13.7372 | 17.8388 | 23.9104 | 27.262 | 29.1177 | 19.7008
6410 | 29.0133 | 25.6493 | 21.5336 | 16.0404 | 11.484 | 9.9845 | 10.6479 | 13.8743 | 18.1742 | 23.9631 | 27.358 | 29.2654 | 19.749
6413 | 28.8765 | 25.7346 | 21.6311 | 16.0421 | 11.4625 | 9.9709 | 10.4996 | 13.8476 | 18.0822 | 23.9071 | 27.109 | 29.0684 | 19.686
6415 | 28.9199 | 25.6274 | 21.575 | 15.9207 | 11.5272 | 9.9743 | 10.4119 | 13.7889 | 18.039 | 23.9616 | 27.427 | 29.3628 | 19.7113
6418 | 28.8555 | 25.7936 | 21.5635 | 15.8986 | 11.263 | 9.7494 | 10.3423 | 13.6056 | 17.7694 | 23.8474 | 27.2518 | 29.1868 | 19.5939
6421 | 29.041 | 25.7274 | 21.5223 | 16.0881 | 11.6023 | 10.1643 | 10.714 | 14.0827 | 18.3294 | 24.1134 | 27.2048 | 29.1889 | 19.8149
6423 | 28.6914 | 25.4495 | 21.81 | 16.3273 | 11.7949 | 10.3726 | 10.909 | 14.3851 | 18.5337 | 23.9688 | 27.1213 | 28.9004 | 19.8553
6425 | 28.9534 | 25.5795 | 21.7266 | 16.1108 | 11.5552 | 10.1663 | 10.6151 | 14.127 | 18.6075 | 24.1641 | 27.3265 | 29.2906 | 19.8519
6426 | 28.6337 | 25.3481 | 21.2359 | 15.8532 | 11.2251 | 9.852 | 10.2884 | 13.9138 | 18.2105 | 23.6189 | 26.6183 | 28.7416 | 19.4616
6429 | 28.3425 | 23.684 | 19.9883 | 15.8493 | 11.9016 | 10.8448 | 11.5031 | 15.3114 | 19.3913 | 23.7894 | 26.0097 | 27.8813 | 19.5414
6430 | 28.3663 | 24.3157 | 20.9165 | 16.1582 | 11.8084 | 10.6768 | 11.3064 | 15.1716 | 19.4795 | 24.2771 | 26.7751 | 28.7502 | 19.8335
6431 | 27.3409 | 23.6023 | 22.1007 | 17.9713 | 15.1609 | 13.6374 | 14.6421 | 18.3256 | 22.3978 | 25.527 | 26.6962 | 26.7151 | 21.1764
6432 | 28.3555 | 24.4579 | 20.8512 | 16.0659 | 11.7667 | 10.6669 | 11.3017 | 15.1023 | 19.343 | 24.1696 | 26.4423 | 28.5462 | 19.7558
6434 | 28.4824 | 23.9926 | 20.1633 | 15.987 | 11.6663 | 10.6184 | 11.4148 | 15.085 | 19.2046 | 23.8595 | 26.0667 | 28.1684 | 19.5591
6436 | 28.168 | 24.3433 | 20.5412 | 16.9374 | 13.0303 | 11.7668 | 12.5421 | 16.3828 | 20.3056 | 24.442 | 26.9749 | 27.9767 | 20.2843
6437 | 28.6728 | 24.0034 | 21.2834 | 17.024 | 13.7893 | 12.4337 | 13.2887 | 17.5333 | 21.8411 | 25.7296 | 28.0648 | 29.2185 | 21.0736
6438 | 28.8839 | 24.2914 | 21.2989 | 16.9089 | 13.2507 | 11.7688 | 12.7872 | 16.7497 | 21.0793 | 25.1567 | 27.8467 | 29.2108 | 20.7694
6440 | 28.23 | 23.9116 | 21.0233 | 16.7251 | 13.3334 | 11.8693 | 12.8579 | 16.9612 | 21.1239 | 25.0139 | 27.5252 | 28.5247 | 20.5916
6442 | 26.6211 | 22.5128 | 19.9251 | 15.6379 | 11.3473 | 10.5227 | 11.0543 | 14.8952 | 18.2352 | 23.1126 | 25.2384 | 27.6611 | 18.897
6443 | 27.6912 | 23.0031 | 18.9718 | 15.1311 | 11.0319 | 10.191 | 10.7487 | 14.2764 | 18.1383 | 22.9639 | 25.4997 | 27.7496 | 18.7831
6445 | 26.926 | 23.5131 | 19.3828 | 14.1403 | 10.1578 | 9.3729 | 9.9768 | 13.2399 | 17.1919 | 22.3239 | 24.8319 | 27.2834 | 18.1951
6447 | 26.1936 | 22.5928 | 18.6494 | 14.1113 | 10.0619 | 9.2029 | 9.6317 | 12.881 | 16.7145 | 21.4629 | 23.8023 | 26.2706 | 17.6312
6448 | 25.7102 | 22.3283 | 18.3667 | 13.89 | 9.7443 | 8.9747 | 9.6252 | 12.8056 | 16.3832 | 21.2306 | 23.9092 | 25.9499 | 17.4098
6450 | 26.1571 | 21.8475 | 18.128 | 14.1883 | 9.9397 | 9.298 | 9.8038 | 13.0308 | 16.7387 | 21.4013 | 23.9203 | 25.9048 | 17.5299
6460 | 29.1935 | 25.8657 | 21.7031 | 16.2626 | 11.6344 | 10.0813 | 10.7024 | 13.7947 | 17.8347 | 24.0706 | 27.3871 | 29.394 | 19.827
6461 | 28.9586 | 25.8697 | 21.7346 | 16.2914 | 11.7335 | 10.3037 | 10.8465 | 14.0435 | 18.1049 | 24.148 | 27.3964 | 29.2675 | 19.8915
6462 | 28.9947 | 25.8443 | 21.6651 | 16.4253 | 11.827 | 10.3535 | 10.9004 | 14.1582 | 18.4205 | 24.1013 | 27.4261 | 29.3189 | 19.9529
6468 | 29.2359 | 25.9071 | 22.2032 | 16.8528 | 12.2079 | 10.8068 | 11.3308 | 14.8039 | 19.0361 | 24.1945 | 27.5746 | 29.4209 | 20.2979
6472 | 29.1661 | 25.5791 | 21.9265 | 16.6066 | 12.1961 | 10.7309 | 11.3682 | 14.8347 | 19.4551 | 24.6538 | 28.078 | 29.75 | 20.3621
6475 | 29.1189 | 25.7516 | 21.8974 | 16.6464 | 12.0673 | 10.6854 | 11.1859 | 14.6622 | 18.8283 | 24.5392 | 28.0205 | 29.6259 | 20.2524
6477 | 28.9523 | 25.9547 | 22.0481 | 16.6158 | 11.9897 | 10.5462 | 11.0281 | 14.4648 | 18.9189 | 24.3274 | 27.6109 | 29.263 | 20.1433
6479 | 28.8519 | 25.6623 | 21.8216 | 16.6445 | 11.9783 | 10.6046 | 11.1882 | 14.7152 | 19.1432 | 24.3546 | 27.5336 | 29.0625 | 20.13
6484 | 28.9737 | 25.2277 | 21.8141 | 16.2731 | 11.9128 | 10.6521 | 11.3773 | 14.9812 | 19.4264 | 24.5727 | 27.69 | 29.424 | 20.1938
6485 | 28.8924 | 25.9766 | 21.7973 | 16.3627 | 11.7601 | 10.1603 | 10.773 | 14.0248 | 18.2932 | 24.2357 | 27.446 | 29.1274 | 19.9041
6488 | 29.0914 | 25.9184 | 21.8105 | 16.3492 | 11.8411 | 10.2477 | 10.8258 | 14.15 | 18.4397 | 23.9709 | 27.3222 | 29.3054 | 19.9394
6490 | 28.4496 | 25.577 | 21.5558 | 16.2159 | 11.6537 | 10.2739 | 10.8903 | 14.1863 | 18.2472 | 23.3631 | 26.1528 | 28.2662 | 19.5693
6501 | 29.817 | 26.4978 | 21.5292 | 15.6113 | 11.1145 | 9.3831 | 10.1809 | 13.2037 | 17.0516 | 23.28 | 26.9053 | 29.9669 | 19.5451
6502 | 29.5583 | 26.3889 | 21.7415 | 15.6819 | 11.1935 | 9.5181 | 10.2476 | 13.2287 | 17.4966 | 23.5667 | 26.9831 | 29.7295 | 19.6112
6503 | 29.6515 | 26.4085 | 21.5853 | 15.7296 | 11.2399 | 9.549 | 10.3384 | 13.3891 | 17.3889 | 23.7051 | 27.1098 | 29.9397 | 19.6696
6505 | 29.6713 | 26.5308 | 21.6285 | 15.8686 | 11.4772 | 9.8326 | 10.3556 | 13.284 | 17.4524 | 23.9337 | 27.2977 | 29.861 | 19.7661
6507 | 29.3979 | 26.0877 | 21.7397 | 16.3186 | 11.7137 | 10.2237 | 11.0476 | 13.9675 | 18.1743 | 24.325 | 27.7696 | 30.1202 | 20.0738
6509 | 29.4533 | 26.3886 | 21.7459 | 16.139 | 11.5971 | 10.0834 | 10.6902 | 13.6594 | 17.7567 | 24.1615 | 27.5203 | 29.7988 | 19.9162
6510 | 29.3565 | 26.2684 | 21.9149 | 16.5799 | 11.8836 | 10.5141 | 10.9702 | 13.9897 | 18.2167 | 24.1874 | 27.7528 | 29.8183 | 20.121
6511 | 29.5306 | 26.788 | 22.3461 | 15.958 | 11.428 | 9.7889 | 10.9356 | 14.3043 | 18.4248 | 24.1706 | 27.6386 | 30.1177 | 20.1193
6513 | 29.3282 | 26.1465 | 22.0478 | 16.7731 | 12.1236 | 10.6737 | 11.245 | 14.524 | 18.7605 | 24.6248 | 27.9763 | 29.6836 | 20.3256
6514 | 29.6456 | 26.809 | 22.3418 | 16.5461 | 12.015 | 10.4214 | 11.413 | 14.8399 | 18.8016 | 24.366 | 27.7624 | 30.3318 | 20.4411
6515 | 29.7512 | 26.3724 | 21.8777 | 16.3297 | 12.026 | 10.6586 | 11.4386 | 14.6951 | 18.8336 | 24.5024 | 28.0197 | 30.2199 | 20.3937
6516 | 29.833 | 26.7025 | 21.9973 | 16.1156 | 11.6361 | 9.9269 | 10.9795 | 14.1225 | 18.0615 | 24.0057 | 27.2204 | 30.2305 | 20.0693
6517 | 29.3233 | 25.9455 | 22.2336 | 17.1385 | 12.5955 | 11.0489 | 11.6079 | 14.8574 | 19.1094 | 24.6088 | 28.191 | 29.7548 | 20.5345
6518 | 29.6649 | 26.3203 | 21.9131 | 16.5173 | 12.1073 | 10.5008 | 11.2282 | 14.4637 | 18.5728 | 24.461 | 27.7919 | 30.3622 | 20.3253
6519 | 29.3322 | 25.9403 | 22.1754 | 17.2461 | 12.7182 | 11.105 | 11.668 | 14.8869 | 19.3165 | 24.7425 | 28.0764 | 29.8846 | 20.591
6521 | 29.5666 | 26.5135 | 21.7099 | 16.4846 | 11.9335 | 10.4101 | 11.0746 | 14.0507 | 18.13 | 24.296 | 27.4703 | 30.0614 | 20.1418
6522 | 29.4765 | 26.1688 | 22.3979 | 17.2165 | 12.7553 | 11.3356 | 11.8046 | 15.0112 | 19.3992 | 24.9047 | 28.0583 | 29.7215 | 20.6875
6525 | 29.6937 | 26.4648 | 22.1902 | 16.5901 | 12.2977 | 10.7113 | 11.5555 | 14.873 | 19.3494 | 24.9477 | 28.0391 | 30.3246 | 20.5864
6528 | 29.3606 | 26.425 | 22.4031 | 16.947 | 12.5992 | 11.096 | 11.6187 | 14.9664 | 19.3952 | 24.7528 | 27.9082 | 30.0017 | 20.6228
6530 | 29.4644 | 26.5032 | 22.4244 | 17.0359 | 12.559 | 11.1036 | 11.7703 | 15.1479 | 19.5654 | 24.9192 | 28.0297 | 29.9981 | 20.7101
6532 | 29.9865 | 26.5537 | 23.1558 | 18.3005 | 14.0448 | 12.9935 | 13.7044 | 17.6234 | 22.2829 | 26.3793 | 29.4326 | 30.3835 | 22.0701
6535 | 29.527 | 26.2445 | 22.5027 | 17.238 | 13.0752 | 11.4332 | 12.2776 | 15.6911 | 20.1373 | 25.1059 | 28.4422 | 30.0081 | 20.9736
6536 | 29.9196 | 26.4106 | 22.6378 | 17.7602 | 13.495 | 11.9823 | 12.9428 | 16.5265 | 20.8987 | 25.3257 | 28.9162 | 30.3974 | 21.4344
6537 | 30.2013 | 27.5583 | 23.3716 | 18.4966 | 13.9961 | 13.0475 | 13.6663 | 17.5627 | 21.7339 | 26.218 | 29.2033 | 30.7889 | 22.1537
6556 | 29.7589 | 26.4343 | 21.4062 | 15.1597 | 10.8625 | 9.199 | 9.9231 | 12.8612 | 16.8786 | 23.0554 | 26.9858 | 29.9576 | 19.3735
6558 | 29.6509 | 26.1865 | 21.2935 | 15.3763 | 10.9629 | 9.3524 | 10.0073 | 12.8592 | 16.892 | 23.0744 | 27.1409 | 29.9869 | 19.3986
6560 | 29.6929 | 26.2212 | 21.4778 | 15.3938 | 10.9539 | 9.4269 | 10.0532 | 13.0373 | 17.1502 | 23.4074 | 27.2751 | 29.9642 | 19.5045
6562 | 29.6824 | 26.158 | 21.2917 | 15.3424 | 11.0606 | 9.4452 | 10.0201 | 13.1044 | 17.1733 | 23.385 | 27.2799 | 29.9615 | 19.492
6564 | 29.4546 | 26.0512 | 21.4697 | 15.521 | 11.1993 | 9.5434 | 10.2412 | 13.1485 | 17.2315 | 23.7782 | 27.2377 | 29.9128 | 19.5658
6566 | 29.2236 | 26.0629 | 21.3799 | 15.777 | 11.3747 | 9.8611 | 10.4381 | 13.2701 | 17.4448 | 23.8552 | 27.2932 | 29.7186 | 19.6416
6567 | 29.504 | 26.0642 | 21.4595 | 15.6168 | 11.0359 | 9.4758 | 10.2355 | 13.2588 | 17.1683 | 23.2565 | 27.0592 | 29.8572 | 19.4993
6568 | 29.2109 | 26.2194 | 21.6407 | 16.2328 | 11.7077 | 10.1453 | 10.7555 | 13.712 | 17.8356 | 24.1344 | 27.4898 | 29.3943 | 19.8732
6569 | 29.0679 | 26.1448 | 21.7041 | 16.3447 | 11.7995 | 10.2752 | 10.8805 | 13.8361 | 18.1377 | 24.2472 | 27.6022 | 29.414 | 19.9545
6575 | 29.3294 | 26.0534 | 21.9151 | 16.7295 | 12.1264 | 10.6323 | 11.1762 | 14.4752 | 18.6162 | 24.4206 | 27.8181 | 29.7869 | 20.2566
6603 | 29.1665 | 25.8696 | 21.7608 | 16.4984 | 11.8458 | 10.462 | 10.9952 | 14.1307 | 18.302 | 24.2954 | 27.4556 | 29.3688 | 20.0126
6606 | 29.125 | 25.9035 | 21.7527 | 16.6592 | 11.9597 | 10.5249 | 11.2096 | 14.5262 | 18.783 | 24.3133 | 27.6417 | 29.4231 | 20.1518
6608 | 29.2939 | 25.9046 | 22.0644 | 16.842 | 12.2482 | 10.9315 | 11.3699 | 14.7435 | 19.1631 | 24.4975 | 27.8135 | 29.5399 | 20.3677
6609 | 29.12 | 25.939 | 22.1003 | 16.8088 | 12.2086 | 10.9251 | 11.3916 | 14.6424 | 19.0565 | 24.4734 | 27.7985 | 29.4244 | 20.324
6612 | 28.8018 | 25.3943 | 21.2431 | 16.6098 | 12.2819 | 10.999 | 11.5253 | 14.8616 | 18.9813 | 24.1118 | 27.2484 | 29.183 | 20.1034
6620 | 29.3493 | 25.8034 | 22.2153 | 17.23 | 12.7124 | 11.4059 | 11.8659 | 15.1987 | 19.5971 | 24.774 | 28.1385 | 29.7573 | 20.6706
6623 | 28.9287 | 25.6092 | 22.0949 | 17.0111 | 12.5469 | 11.2411 | 11.7419 | 15.2394 | 19.4917 | 24.6684 | 28.0474 | 29.5336 | 20.5129
6628 | 29.59 | 26.3234 | 22.6971 | 17.5898 | 13.0855 | 11.5669 | 11.962 | 15.3438 | 19.9314 | 25.1824 | 28.3007 | 29.7503 | 20.9436
6630 | 30.0036 | 26.3182 | 22.7134 | 17.5715 | 13.19 | 11.9172 | 12.46 | 16.2605 | 20.6207 | 25.4908 | 28.9825 | 30.4813 | 21.3341
6635 | 29.7028 | 25.8269 | 22.771 | 17.8749 | 14.0281 | 12.8278 | 13.4822 | 17.484 | 21.932 | 26.2898 | 29.207 | 30.3043 | 21.8109
6638 | 29.3687 | 25.4725 | 22.2223 | 17.0832 | 13.4332 | 12.2323 | 12.8371 | 16.623 | 21.2527 | 25.7693 | 28.7993 | 29.9929 | 21.2572
6639 | 28.8903 | 24.7561 | 21.8876 | 16.9704 | 13.4353 | 12.3222 | 12.9409 | 16.9611 | 21.3365 | 25.6764 | 28.4632 | 29.7783 | 21.1182
6640 | 29.4085 | 25.1303 | 22.3887 | 17.6415 | 14.0149 | 12.8939 | 13.4306 | 17.716 | 22.1612 | 26.2498 | 28.9586 | 30.254 | 21.6873
6642 | 28.4323 | 23.9274 | 22.1414 | 18.0459 | 15.0789 | 13.8825 | 14.5824 | 18.7102 | 23.0259 | 26.6504 | 29.1392 | 29.2 | 21.9014
6646 | 27.7251 | 23.2616 | 22.3752 | 17.8073 | 15.2056 | 13.8967 | 14.8884 | 18.967 | 23.2128 | 26.5947 | 28.3544 | 27.699 | 21.6656
6701 | 29.4703 | 25.75 | 23.5094 | 19.1042 | 15.004 | 13.8913 | 14.8095 | 18.8748 | 23.2236 | 27.044 | 29.7847 | 30.3045 | 22.5642
6705 | 28.8663 | 25.3071 | 23.0453 | 18.6492 | 15.2004 | 14.0561 | 14.8159 | 19.0993 | 23.4503 | 27.0147 | 29.6521 | 29.7741 | 22.4109
6707 | 29.1928 | 25.969 | 23.8837 | 19.7623 | 15.8881 | 14.637 | 15.4322 | 19.7792 | 23.5777 | 27.4043 | 29.8792 | 29.9622 | 22.9473
6710 | 27.9834 | 24.673 | 23.2368 | 19.6252 | 16.1981 | 14.8263 | 16.1143 | 20.1828 | 24.0093 | 27.6343 | 29.7734 | 29.2225 | 22.79
6713 | 27.776 | 25.0722 | 24.4343 | 20.9084 | 17.2181 | 15.2923 | 17.2039 | 20.9414 | 24.2396 | 27.4062 | 29.0729 | 28.5343 | 23.175
6714 | 27.2729 | 24.0373 | 23.5537 | 20.4019 | 16.905 | 15.1915 | 16.9407 | 20.7698 | 24.3977 | 27.8361 | 29.7375 | 28.9738 | 23.0015
6716 | 27.2027 | 23.9234 | 23.0305 | 19.7468 | 16.4973 | 14.9881 | 16.5763 | 20.6104 | 24.3267 | 27.742 | 29.676 | 28.7352 | 22.7546
6718 | 27.5139 | 24.9662 | 24.298 | 20.7584 | 17.063 | 15.2643 | 16.9857 | 20.6922 | 23.8686 | 27.0867 | 28.7872 | 28.59 | 22.9895
6720 | 27.3425 | 24.797 | 24.0474 | 20.7242 | 16.992 | 15.3386 | 16.9711 | 20.5448 | 23.7115 | 26.7555 | 28.3585 | 28.0705 | 22.8045
6721 | 26.9623 | 23.4105 | 23.3884 | 20.5628 | 17.109 | 15.5605 | 17.018 | 20.7825 | 24.2566 | 27.4572 | 29.1581 | 27.7 | 22.7805
6722 | 26.8351 | 23.3056 | 23.4397 | 20.2859 | 16.8262 | 15.3085 | 16.9538 | 20.7786 | 24.2634 | 27.6066 | 29.2603 | 27.9311 | 22.7329
6725 | 24.8766 | 21.769 | 22.8162 | 21.4982 | 18.3095 | 16.9073 | 18.2171 | 21.6484 | 24.62 | 26.9889 | 28.6706 | 26.1752 | 22.7081
6726 | 24.113 | 21.012 | 22.7282 | 21.5471 | 18.6752 | 17.3362 | 18.7335 | 21.8516 | 24.3291 | 26.6026 | 27.8088 | 24.9069 | 22.4703
6728 | 24.7726 | 22.6753 | 23.3686 | 22.0975 | 19.3053 | 18.0048 | 19.2897 | 22.2228 | 24.6482 | 26.6728 | 26.7236 | 24.9743 | 22.8963
6740 | 22.5145 | 20.4441 | 22.4349 | 22.1084 | 20.303 | 19.2398 | 20.1042 | 22.5804 | 23.8428 | 25.1736 | 24.8546 | 22.337 | 22.1614
6743 | 23.7204 | 21.759 | 23.2416 | 22.4664 | 20.163 | 18.8868 | 19.8064 | 22.6768 | 24.4137 | 25.3972 | 25.2328 | 23.7174 | 22.6235
6751 | 26.7836 | 23.4165 | 22.7005 | 19.6675 | 16.4211 | 15.0284 | 16.5498 | 20.3967 | 24.3034 | 27.3486 | 29.1115 | 28.2162 | 22.4953
6753 | 27.364 | 23.2783 | 22.9057 | 19.331 | 16.2216 | 14.9596 | 16.2305 | 20.2482 | 24.0423 | 27.2953 | 29.0235 | 28.142 | 22.4202
6754 | 27.3858 | 23.6947 | 22.7198 | 19.0197 | 16.1203 | 14.5371 | 16.0209 | 19.9899 | 23.9744 | 27.4426 | 29.2055 | 28.4836 | 22.3829
6758 | 26.9912 | 23.2664 | 22.9749 | 20.1692 | 16.7161 | 15.353 | 16.7349 | 20.5139 | 23.9521 | 27.2544 | 29.1323 | 27.6986 | 22.5631
6760 | 27.1418 | 23.9516 | 23.7617 | 20.3225 | 16.8674 | 15.3805 | 16.9987 | 20.7835 | 24.2731 | 27.5481 | 29.4512 | 28.3692 | 22.9041
6762 | 26.6316 | 23.355 | 22.8546 | 20.6218 | 17.4419 | 15.7235 | 17.3715 | 20.9185 | 24.0599 | 26.6795 | 28.3043 | 26.8142 | 22.5647
6765 | 24.9812 | 22.8492 | 23.5779 | 22.1672 | 19.0895 | 17.6869 | 19.0253 | 21.8624 | 24.5705 | 26.7169 | 27.1645 | 25.2928 | 22.9154
6770 | 25.7892 | 22.7159 | 23.7097 | 22.0438 | 18.7314 | 17.3597 | 18.7346 | 21.8312 | 24.448 | 26.2735 | 26.2657 | 24.7441 | 22.7206
6798
6799
6907 | 29.85 | 26.6682 | 21.4723 | 15.2419 | 10.8829 | 8.9442 | 10.0198 | 13.3244 | 17.3146 | 23.4131 | 27.242 | 30.2472 | 19.5517
7000 | 22.873 | 19.701 | 14.9517 | 9.4211 | 5.9981 | 4.6559 | 5.4833 | 8.9636 | 12.7969 | 17.3304 | 21.5131 | 24.231 | 13.9933
7004 | 22.8584 | 19.6977 | 14.9222 | 9.2914 | 5.9498 | 4.6592 | 5.516 | 8.8853 | 12.852 | 17.2947 | 21.311 | 24.1562 | 13.9495
7005 | 22.8584 | 19.6977 | 14.9222 | 9.2914 | 5.9498 | 4.6592 | 5.516 | 8.8853 | 12.852 | 17.2947 | 21.311 | 24.1562 | 13.9495
7007 | 22.8584 | 19.6977 | 14.9222 | 9.2914 | 5.9498 | 4.6592 | 5.516 | 8.8853 | 12.852 | 17.2947 | 21.311 | 24.1562 | 13.9495
7008 | 22.873 | 19.701 | 14.9517 | 9.4211 | 5.9981 | 4.6559 | 5.4833 | 8.9636 | 12.7969 | 17.3304 | 21.5131 | 24.231 | 13.9933
7009 | 22.873 | 19.701 | 14.9517 | 9.4211 | 5.9981 | 4.6559 | 5.4833 | 8.9636 | 12.7969 | 17.3304 | 21.5131 | 24.231 | 13.9933
7010 | 22.9155 | 19.7361 | 14.9351 | 9.4632 | 6.024 | 4.7205 | 5.4674 | 8.8676 | 12.7657 | 17.429 | 21.4946 | 24.1658 | 13.9987
7011 | 22.9651 | 19.733 | 14.8168 | 9.5104 | 6.0523 | 4.6963 | 5.4703 | 8.9833 | 12.7996 | 17.5218 | 21.7029 | 24.208 | 14.0383
7012 | 22.7459 | 19.5903 | 14.5799 | 9.2969 | 5.9714 | 4.6255 | 5.4104 | 8.8399 | 12.707 | 17.3261 | 21.3468 | 23.8863 | 13.8605
7015 | 22.8955 | 19.8363 | 14.8785 | 9.3689 | 6.0378 | 4.6 | 5.5499 | 8.8657 | 12.9853 | 17.1901 | 21.4155 | 24.2293 | 13.9877
7016 | 23.0478 | 20.031 | 14.9262 | 9.4039 | 6.1249 | 4.724 | 5.4943 | 8.9481 | 13.0163 | 17.3151 | 21.4474 | 24.4738 | 14.0794
7017 | 23.0591 | 19.8322 | 14.9669 | 9.6282 | 6.2364 | 4.7834 | 5.6165 | 9.0763 | 13.0479 | 17.4326 | 21.5092 | 24.4603 | 14.1374
7018 | 22.9908 | 20.102 | 15.075 | 9.465 | 6.1364 | 4.6505 | 5.5719 | 8.9331 | 13.1229 | 17.3467 | 21.4355 | 24.3466 | 14.098
7019 | 22.9455 | 20.0386 | 15.126 | 9.3533 | 5.9673 | 4.6408 | 5.604 | 8.9742 | 13.1547 | 17.3637 | 21.2555 | 24.1939 | 14.0515
7020 | 22.99 | 20.1483 | 15.1244 | 9.3848 | 5.9215 | 4.5525 | 5.5564 | 8.9873 | 13.2528 | 17.4389 | 21.2073 | 24.2035 | 14.064
7021 | 22.8267 | 19.9221 | 15.1198 | 9.4421 | 5.9254 | 4.5972 | 5.5678 | 8.9228 | 13.1396 | 17.405 | 21.3186 | 24.2124 | 14.0333
7022 | 22.6211 | 19.8413 | 14.9862 | 9.2351 | 5.8436 | 4.4572 | 5.4544 | 8.8069 | 12.7855 | 17.0676 | 21.227 | 23.7982 | 13.8437
7023 | 22.6211 | 19.8413 | 14.9862 | 9.2351 | 5.8436 | 4.4572 | 5.4544 | 8.8069 | 12.7855 | 17.0676 | 21.227 | 23.7982 | 13.8437
7024 | 22.99 | 20.1483 | 15.1244 | 9.3848 | 5.9215 | 4.5525 | 5.5564 | 8.9873 | 13.2528 | 17.4389 | 21.2073 | 24.2035 | 14.064
7025 | 23.1012 | 19.8764 | 15.0283 | 9.5389 | 6.2401 | 4.7635 | 5.6128 | 8.9827 | 13.1293 | 17.4907 | 21.5688 | 24.6328 | 14.1638
7026 | 22.9814 | 19.8038 | 15.2699 | 9.6441 | 6.2304 | 4.6939 | 5.5956 | 9.0973 | 13.2536 | 17.6339 | 21.5447 | 24.6391 | 14.199
7027 | 23.0879 | 19.9625 | 15.3925 | 9.6997 | 6.2782 | 4.7369 | 5.4916 | 9.0578 | 13.0705 | 17.764 | 21.8374 | 24.8441 | 14.2686
7030 | 23.6437 | 20.6914 | 15.514 | 9.9148 | 6.3206 | 4.781 | 5.5002 | 9.0633 | 13.1754 | 18.2077 | 22.3513 | 24.8585 | 14.5018
7050 | 22.7023 | 19.7043 | 14.9463 | 9.2697 | 5.8662 | 4.5988 | 5.4712 | 8.8128 | 12.9201 | 17.1767 | 20.9205 | 23.9554 | 13.862
7052 | 22.4569 | 19.6908 | 14.6669 | 9.3146 | 5.888 | 4.4894 | 5.4639 | 8.7707 | 12.931 | 17.0935 | 20.7653 | 23.5829 | 13.7595
7053 | 22.7023 | 19.7043 | 14.9463 | 9.2697 | 5.8662 | 4.5988 | 5.4712 | 8.8128 | 12.9201 | 17.1767 | 20.9205 | 23.9554 | 13.862
7054 | 22.5068 | 19.2003 | 14.0862 | 8.955 | 5.7407 | 4.4021 | 5.2149 | 8.6351 | 12.2638 | 16.7931 | 20.7515 | 23.2548 | 13.4837
7055 | 22.4569 | 19.6908 | 14.6669 | 9.3146 | 5.888 | 4.4894 | 5.4639 | 8.7707 | 12.931 | 17.0935 | 20.7653 | 23.5829 | 13.7595
7109 | 22.4067 | 18.9062 | 13.4451 | 8.4345 | 5.5005 | 4.1076 | 5.0933 | 8.3064 | 12.2567 | 16.5874 | 20.2606 | 22.4929 | 13.1498
7112 | 22.0404 | 19.1266 | 13.7322 | 8.625 | 5.5408 | 4.1278 | 5.0706 | 8.2819 | 12.2078 | 16.4006 | 20.3342 | 22.3957 | 13.157
7113 | 22.4702 | 19.2516 | 13.8308 | 8.7062 | 5.644 | 4.2396 | 5.1595 | 8.3737 | 12.0442 | 16.7492 | 20.6991 | 23.1679 | 13.3613
7116 | 22.7257 | 19.1126 | 13.7951 | 8.6063 | 5.4416 | 4.1639 | 5.1086 | 8.3445 | 12.2166 | 16.6566 | 20.5961 | 23.1637 | 13.3276
7117 | 22.6552 | 19.0069 | 13.7336 | 8.5221 | 5.4387 | 4.1247 | 5.0592 | 8.3334 | 12.3159 | 16.6143 | 20.3928 | 22.7204 | 13.2431
7120 | 23.2731 | 20.2596 | 15.532 | 9.7525 | 6.29 | 4.635 | 5.4238 | 9.0168 | 13.0959 | 17.6779 | 21.7698 | 25.1197 | 14.3205
7140 | 23.612 | 20.1676 | 14.9596 | 9.5915 | 6.0256 | 4.7621 | 5.5598 | 8.9181 | 12.8794 | 18.1078 | 22.2382 | 25.094 | 14.3263
7150 | 22.5984 | 19.0618 | 13.5481 | 8.5303 | 5.3787 | 4.0731 | 5.0676 | 8.1477 | 12.1373 | 16.9144 | 20.4173 | 22.7359 | 13.2175
7155 | 22.2129 | 19.2619 | 14.0138 | 8.8366 | 5.661 | 4.2303 | 5.2499 | 8.4614 | 12.5859 | 16.8156 | 20.3704 | 22.7405 | 13.37
7162 | 22.2129 | 19.2619 | 14.0138 | 8.8366 | 5.661 | 4.2303 | 5.2499 | 8.4614 | 12.5859 | 16.8156 | 20.3704 | 22.7405 | 13.37
7163 | 22.663 | 19.3026 | 14.0736 | 9.0075 | 5.5652 | 4.1444 | 5.271 | 8.4378 | 12.6167 | 17.0156 | 20.6712 | 23.0276 | 13.483
7170 | 22.965 | 20.1102 | 15.222 | 9.49 | 6.066 | 4.6745 | 5.5881 | 8.9669 | 13.1409 | 17.4119 | 21.4188 | 24.3684 | 14.1186
7171 | 22.7971 | 19.8231 | 15.0341 | 9.3697 | 6.1188 | 4.6803 | 5.5489 | 9.0247 | 12.9438 | 17.1997 | 21.2893 | 24.2217 | 14.0043
7172 | 22.3925 | 19.6789 | 14.7971 | 9.3401 | 6.1263 | 4.6839 | 5.539 | 8.9985 | 13.2286 | 17.1885 | 21.0221 | 23.9858 | 13.9151
7173 | 22.4691 | 19.7698 | 14.7943 | 9.2428 | 6.0032 | 4.5982 | 5.5388 | 8.917 | 13.1965 | 17.3418 | 21.1238 | 23.9768 | 13.9143
7176 | 22.2373 | 19.5527 | 14.8678 | 9.2768 | 6.0248 | 4.6347 | 5.5876 | 8.9691 | 13.2234 | 17.2743 | 20.8025 | 23.7409 | 13.8493
7177 | 22.2727 | 19.5359 | 14.9789 | 9.4822 | 6.0377 | 4.5616 | 5.5988 | 9.0043 | 13.3163 | 17.4659 | 20.8558 | 23.8609 | 13.9143
7178 | 22.2831 | 19.3787 | 14.6701 | 9.3718 | 5.918 | 4.5031 | 5.5585 | 8.8798 | 13.1459 | 17.7805 | 21.1446 | 24.142 | 13.898
7179 | 22.3746 | 18.9864 | 14.4801 | 9.2101 | 5.7174 | 4.2874 | 5.3868 | 8.7616 | 13.0999 | 17.3189 | 20.7994 | 23.6793 | 13.6752
7180 | 22.3899 | 19.1064 | 14.3697 | 9.115 | 5.7665 | 4.3764 | 5.3587 | 8.7813 | 12.8288 | 17.4113 | 21.2251 | 23.9275 | 13.7214
7182 | 22.602 | 19.1859 | 13.8434 | 8.8722 | 5.5905 | 4.2953 | 5.3538 | 8.7362 | 12.7188 | 17.1743 | 20.7142 | 23.5662 | 13.5544
7183 | 22.7428 | 19.3075 | 14.0314 | 8.7429 | 5.5532 | 4.1914 | 5.2977 | 8.6175 | 12.6788 | 17.4514 | 21.0504 | 23.4818 | 13.5956
7184 | 22.8846 | 19.5973 | 14.1851 | 9.0657 | 5.8134 | 4.4416 | 5.4212 | 8.7577 | 12.6611 | 17.3221 | 20.9959 | 23.8563 | 13.7502
7186 | 22.635 | 19.669 | 14.7481 | 9.3612 | 5.8882 | 4.4276 | 5.462 | 8.8182 | 12.9497 | 17.4621 | 21.4199 | 24.2591 | 13.925
7190 | 22.5422 | 19.4014 | 15.5776 | 9.9356 | 6.4103 | 4.8861 | 5.7622 | 9.2319 | 13.5904 | 17.3122 | 21.3524 | 24.7236 | 14.2271
7209 | 23.1644 | 19.7885 | 15.5643 | 9.6692 | 6.2918 | 4.5561 | 5.2583 | 8.8608 | 13.1684 | 17.4034 | 21.7224 | 24.8284 | 14.1897
7210 | 22.9043 | 20.0433 | 15.7538 | 9.8139 | 6.3968 | 4.6905 | 5.5318 | 8.8775 | 13.2349 | 17.3527 | 21.7499 | 24.8097 | 14.2633
7211 | 24.6768 | 21.4477 | 16.8196 | 10.5256 | 6.7863 | 4.9788 | 5.6847 | 9.111 | 13.5012 | 18.3299 | 22.8354 | 26.2318 | 15.0774
7212 | 24.0012 | 20.9129 | 16.4345 | 10.1046 | 6.771 | 4.8271 | 5.4662 | 8.7131 | 12.6093 | 17.9419 | 22.2961 | 25.6194 | 14.6415
7213 | 22.2074 | 19.359 | 15.5672 | 9.9086 | 6.6293 | 4.9319 | 5.8348 | 9.4877 | 13.4452 | 17.5137 | 21.4391 | 24.407 | 14.2276
7214 | 22.5571 | 19.4925 | 16.1177 | 10.2657 | 6.7728 | 5.0637 | 5.7658 | 9.2682 | 13.4115 | 17.8303 | 21.8763 | 24.772 | 14.4328
7215 | 22.1208 | 19.3082 | 15.8329 | 10.2326 | 6.7187 | 5.1472 | 6.0517 | 9.6645 | 13.9586 | 17.6937 | 21.1363 | 24.2482 | 14.3428
7216 | 21.7998 | 19.1621 | 15.8421 | 10.5221 | 6.8847 | 5.1216 | 6.0328 | 9.3425 | 13.3439 | 17.6224 | 21.0777 | 24.0002 | 14.2293
7248 | 24.2069 | 21.0558 | 16.6238 | 10.5412 | 6.7944 | 4.9989 | 5.6153 | 8.9169 | 12.9218 | 18.2123 | 22.5772 | 26.0679 | 14.8777
7249 | 24.5436 | 21.5059 | 16.8913 | 10.6457 | 6.8861 | 5.0404 | 5.7073 | 9.012 | 13.1794 | 18.3762 | 22.727 | 26.5639 | 15.0899
7250 | 24.2932 | 21.2586 | 16.7073 | 10.4901 | 6.8128 | 4.9504 | 5.5995 | 8.7768 | 13.0391 | 18.1392 | 22.6342 | 26.1312 | 14.9027
7252 | 24.3057 | 21.2005 | 16.7409 | 10.6795 | 6.9055 | 5.1432 | 5.8943 | 9.4082 | 13.2968 | 19.0892 | 22.8039 | 26.618 | 15.1738
7253 | 25.4539 | 22.2163 | 17.8395 | 11.4574 | 7.2915 | 5.3789 | 6.3789 | 9.8922 | 14.1461 | 19.9694 | 23.9495 | 27.7712 | 15.9787
7254 | 24.4363 | 21.2703 | 16.8233 | 10.8452 | 7.0059 | 5.345 | 6.211 | 9.6283 | 13.6752 | 19.0945 | 22.9843 | 26.7978 | 15.3431
7255 | 24.4047 | 21.625 | 16.1791 | 10.884 | 7.2159 | 5.6395 | 6.7459 | 10.0603 | 14.23 | 18.8452 | 22.6342 | 24.8692 | 15.2777
7256 | 23.9171 | 20.7825 | 15.3423 | 10.3905 | 6.8157 | 5.4291 | 6.1568 | 9.4454 | 13.5517 | 18.1874 | 21.6601 | 23.973 | 14.6376
7257 | 23.6332 | 21.0153 | 16.5566 | 10.9107 | 7.0786 | 5.5344 | 6.6234 | 9.8357 | 14.3476 | 18.9119 | 22.8866 | 25.2206 | 15.2129
7258 | 24.7981 | 21.5947 | 16.9487 | 10.6548 | 6.9559 | 5.07 | 5.7157 | 8.9551 | 13.331 | 18.4781 | 22.6979 | 26.6309 | 15.1526
7259 | 22.7035 | 20.0955 | 15.9013 | 9.6883 | 6.4813 | 4.5885 | 5.2286 | 8.4115 | 12.1199 | 17.1538 | 21.3835 | 24.729 | 14.0404
7260 | 23.6878 | 20.6282 | 16.291 | 10.4654 | 6.929 | 5.0832 | 5.9847 | 9.2889 | 13.0865 | 18.1302 | 22.1616 | 25.9317 | 14.8057
7261 | 22.8192 | 20.0168 | 15.9591 | 10.2382 | 6.7416 | 4.9825 | 5.8313 | 9.0075 | 12.5856 | 17.2893 | 21.3307 | 24.9149 | 14.3097
7262 | 24.6386 | 21.4057 | 17.0078 | 11.1395 | 7.1854 | 5.3592 | 6.3501 | 9.7005 | 13.7862 | 18.9838 | 22.9919 | 26.8611 | 15.4508
7263 | 22.7839 | 20.0995 | 15.9654 | 10.0655 | 6.6738 | 4.88 | 5.6244 | 8.8519 | 12.3804 | 17.0574 | 21.5729 | 24.9912 | 14.2455
7264 | 23.6897 | 20.594 | 16.5705 | 10.9248 | 6.963 | 5.3172 | 6.3385 | 9.6326 | 13.5844 | 18.406 | 22.1822 | 25.9911 | 15.0162
7265 | 22.9067 | 19.9957 | 16.0006 | 10.4696 | 6.8799 | 5.0923 | 5.9883 | 9.2403 | 13.0639 | 17.7282 | 21.4969 | 25.2667 | 14.5108
7267 | 23.8628 | 21.055 | 16.4584 | 10.4013 | 6.7473 | 5.0391 | 5.7042 | 9.2064 | 12.8635 | 18.5182 | 22.4895 | 26.1853 | 14.8776
7268 | 23.6387 | 20.8527 | 16.3398 | 10.2109 | 6.6676 | 4.9555 | 5.6359 | 8.918 | 12.5274 | 18.1692 | 21.9398 | 25.7832 | 14.6366
7270 | 24.631 | 21.4114 | 16.6874 | 10.7846 | 6.9821 | 5.1932 | 5.9574 | 9.5089 | 13.5685 | 19.1004 | 22.8706 | 26.7562 | 15.2876
7275 | 24.5303 | 21.4523 | 16.7952 | 10.8297 | 6.8624 | 5.1352 | 5.8309 | 9.3727 | 13.4199 | 18.7534 | 22.6929 | 26.6198 | 15.1912
7276 | 24.4741 | 21.334 | 16.8476 | 10.8385 | 6.8776 | 5.0671 | 5.7894 | 9.2652 | 13.2434 | 18.813 | 22.7748 | 26.5255 | 15.1542
7277 | 24.4381 | 21.276 | 16.8482 | 10.7886 | 6.8633 | 5.1041 | 5.7387 | 9.1907 | 13.2151 | 18.647 | 22.767 | 26.6199 | 15.1247
7290 | 24.6704 | 21.364 | 16.8392 | 10.707 | 6.9159 | 5.0593 | 5.717 | 9.209 | 13.3995 | 18.7229 | 22.8001 | 26.7248 | 15.1774
7291 | 24.5585 | 21.3762 | 16.7148 | 10.7554 | 6.9161 | 5.051 | 5.7171 | 9.2344 | 13.3981 | 18.6275 | 22.7666 | 26.7532 | 15.1557
7292 | 24.2869 | 21.3287 | 16.5108 | 10.7065 | 6.8143 | 4.9994 | 5.6884 | 9.1116 | 13.1859 | 18.8527 | 22.7151 | 26.5198 | 15.06
7300 | 25.1228 | 21.8602 | 17.0779 | 10.6982 | 6.9951 | 5.1054 | 5.7704 | 9.1448 | 13.4173 | 18.7889 | 22.8757 | 27.0164 | 15.3228
7301 | 24.9245 | 21.7964 | 16.9596 | 10.7042 | 7.0381 | 5.1372 | 5.7449 | 9.1379 | 13.4967 | 18.8894 | 23.0624 | 27.0141 | 15.3255
7302 | 25.0121 | 21.704 | 16.803 | 10.4365 | 6.9056 | 5.0391 | 5.6908 | 9.3931 | 13.4333 | 18.666 | 23.0871 | 26.8352 | 15.2505
7303 | 24.5949 | 21.5787 | 16.7991 | 10.6945 | 6.957 | 5.0761 | 5.7132 | 9.1531 | 13.3071 | 18.7004 | 22.9218 | 26.9455 | 15.2035
7304 | 22.8771 | 20.5271 | 15.6244 | 9.9581 | 6.2769 | 4.5553 | 5.1402 | 8.2708 | 12.1897 | 17.8068 | 21.6798 | 25.5447 | 14.2042
7305 | 24.2014 | 21.1214 | 16.546 | 10.6871 | 6.8281 | 5.1225 | 5.7657 | 9.1743 | 13.122 | 19.0665 | 22.7076 | 26.5022 | 15.0704
7306 | 23.2585 | 20.5717 | 15.9313 | 10.2634 | 6.5334 | 4.8347 | 5.3958 | 8.7294 | 12.4843 | 18.4371 | 22.1115 | 25.9171 | 14.539
7307 | 24.6715 | 21.5166 | 16.8947 | 10.9784 | 6.9954 | 5.2588 | 6.0057 | 9.491 | 13.3615 | 19.2153 | 22.7573 | 26.6802 | 15.3189
7310 | 24.5144 | 21.3207 | 16.6731 | 10.9301 | 6.8948 | 5.1965 | 5.8578 | 9.2691 | 13.0293 | 19.0624 | 22.6115 | 26.5998 | 15.1633
7315 | 22.5396 | 20.2032 | 15.7053 | 10.0014 | 6.4384 | 4.7066 | 5.1359 | 8.5369 | 12.3203 | 18.1514 | 21.7535 | 25.2795 | 14.231
7316 | 23.8277 | 20.9157 | 16.4125 | 10.6895 | 6.6617 | 5.0369 | 5.605 | 9.1229 | 12.9131 | 18.713 | 22.0163 | 25.9973 | 14.826
7320 | 24.2884 | 20.8394 | 16.5917 | 11.0585 | 6.8803 | 5.1284 | 5.8474 | 9.2434 | 13.2144 | 18.7414 | 22.2895 | 26.2138 | 15.0281
7321 | 21.812 | 19.2489 | 14.1366 | 9.2239 | 5.7174 | 4.2033 | 4.841 | 7.9026 | 11.5444 | 16.7687 | 20.2077 | 23.4945 | 13.2584
7322 | 24.3189 | 20.9141 | 16.6154 | 11.0908 | 6.8883 | 5.1548 | 5.8672 | 9.2853 | 13.2192 | 18.781 | 22.2209 | 26.3052 | 15.0551
7325 | 22.7574 | 19.9081 | 15.2442 | 9.9083 | 6.3256 | 4.7788 | 5.2413 | 8.5742 | 12.1907 | 17.9786 | 21.3084 | 25.08 | 14.108
7330 | 23.3828 | 20.2296 | 15.2473 | 9.9873 | 6.5681 | 4.9411 | 5.7616 | 8.9452 | 12.3973 | 17.7593 | 21.4624 | 24.4994 | 14.2651
7331 | 24.7918 | 20.8203 | 16.1711 | 10.8625 | 6.8675 | 5.1955 | 6.0504 | 9.3762 | 13.267 | 18.6824 | 22.1297 | 25.9548 | 15.0141
7467 | 20.5859 | 18.0423 | 12.5849 | 8.1235 | 4.8149 | 3.8267 | 4.3523 | 7.0642 | 10.4467 | 14.5027 | 18.5979 | 20.6332 | 11.9646
7468 | 22.6371 | 19.0923 | 13.5319 | 8.4653 | 5.2318 | 4.0996 | 4.8321 | 7.8994 | 11.3278 | 16.4709 | 20.3923 | 22.7447 | 13.0604
7469 | 22.0529 | 18.964 | 13.2891 | 8.4776 | 5.1891 | 4.0916 | 4.7468 | 7.7374 | 11.0917 | 16.2719 | 20.0143 | 22.3579 | 12.857
7470 | 21.3924 | 18.6534 | 13.331 | 8.4228 | 5.1982 | 3.9791 | 4.591 | 7.5484 | 10.9035 | 15.5052 | 19.5934 | 21.8288 | 12.5789

## Assumptions (hidden)
Component | Value | Units | Comments | Month | Days per month
Panel rating | 0.25 | kW |  | January | 31
Panel area | 1.6 | m2 |  | February | 28
Panel efficiency | 15% | - |  | March | 31
System efficiency | 80% | - |  | April | 30
System degradation | 0.5% | %/a |  | May | 31
Electricity price increase per year | 2.5% | %/a |  | June | 30
Unit cost of system | 1650 | $/kW | Average of all system costs for 10 kW system from Solar Choice March 2014 | July | 31
Inverter Replacement Cost Estimate | 500 | $/kW |  | August | 31
Inverter Replacement Cost | 2500 | $ |  | September | 30
Annual OPEX (% of CAPEX) | 1% |  |  | October | 31
Estimated Annual OPEX (year 1) | 82.5 |  |  | November | 30
Annual escalation of OPEX | 3% |  |  | December | 31
Interest Rate | 5.25%
Discount Rate | 5.25%
IRR for likely investment | 10%
IRR guess | 10%
Taxation rate | 30% |  | Corporate tax rate

## check (hidden)
| Postcode | 4512
|  | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
|  | January | February | March | April | May | June | July | August | September | October | November | December | Annual
Solar Rad (MJ/m2) |  | 22.6512 | 20.1592 | 19.5529 | 16.0577 | 13.1652 | 11.5829 | 13.036 | 15.8786 | 19.8975 | 20.9774 | 22.6196 | 23.6977 | 18.273 |  | What about system orientation?
Solar Rad (kWh/m2) |  | 6.292 | 5.5998 | 5.4314 | 4.4605 | 3.657 | 3.2175 | 3.6211 | 4.4107 | 5.5271 | 5.8271 | 6.2832 | 6.5827 |  |  | Compare to PVsyst results
PSH |  | 6.292 | 5.5998 | 5.4314 | 4.4605 | 3.657 | 3.2175 | 3.6211 | 4.4107 | 5.5271 | 5.8271 | 6.2832 | 6.5827
Generation estimate | Chris | 4681.248 | 3763.0507 | 4040.9327 | 3211.5398 | 2720.808 | 2316.58 | 2694.1067 | 3281.5773 | 3979.4998 | 4335.3293 | 4523.92 | 4897.5247
Generation estimate | peak | 3343.7486 | 2687.8933 | 2886.3805 | 2293.957 | 1943.4343 | 1654.7 | 1924.3619 | 2343.9838 | 2842.4999 | 3096.6638 | 3231.3714 | 3498.2319
Generation estimate | off-peak | 1337.4994 | 1075.1573 | 1154.5522 | 917.5828 | 777.3737 | 661.88 | 769.7448 | 937.5935 | 1136.9999 | 1238.6655 | 1292.5486 | 1399.2928
| Month | January | February | March | April | May | June | July | August | September | October | November | December | Total
Calculated values | Peak generation (kWh) | 3210.2554 | 2580.584 | 2771.1469 | 2202.3749 | 1865.8462 | 1588.6391 | 1847.5352 | 2250.4045 | 2729.0182 | 2973.0351 | 3102.3647 | 3358.5713 | 30479.7756
Calculated values | Off peak generation (kWh) | 1284.1022 | 1032.2336 | 1108.4588 | 880.95 | 746.3385 | 635.4556 | 739.0141 | 900.1618 | 1091.6073 | 1189.214 | 1240.9459 | 1343.4285 | 12191.9102
Total | Andrew | 4494.3576 | 3612.8176 | 3879.6057 | 3083.3249 | 2612.1846 | 2224.0947 | 2586.5493 | 3150.5663 | 3820.6254 | 4162.2491 | 4343.3106 | 4701.9998
PVsyst outputs | PVsyst outputs | 4401 | 3719 | 4044 | 3690 | 3378 | 3002 | 3456 | 4001 | 4324 | 4506 | 4468 | 5188
Chris Total vs Andrew Total |  | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 |  | Andrew's estimate approx 4% lower - ok
Chris Peak vs Andrew Peak |  | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416
Chris Off-peak vs Andrew Off-peak |  | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416 | 1.0416
Chris vs PVsyst |  | 1.0637 | 1.0118 | 0.99924 | 0.87034 | 0.80545 | 0.77168 | 0.77954 | 0.82019 | 0.92033 | 0.96212 | 1.0125 | 0.94401
| GlobHor | January: Tamb; February: GlobInc; March: GlobEff; April: EArray; May: E_Grid; June: EffArrR; July: EffSysR
| kWh/m² | January: °C; February: kWh/m²; March: kWh/m²; April: MWh; May: MWh; June: %; July: %
January | 197.2 | 24.9 | 190.8 | 184.8 | 4.515 | 4.401 | 12.43 | 12.12 |  | 4401
February | 159.5 | 24.6 | 160 | 155.3 | 3.812 | 3.719 | 12.52 | 12.21 |  | 3719
March | 162.7 | 23.4 | 171.9 | 166.6 | 4.144 | 4.044 | 12.66 | 12.36 |  | 4044
April | 136.7 | 21.1 | 155.3 | 150.4 | 3.783 | 3.69 | 12.8 | 12.49 |  | 3690
May | 114.5 | 18.2 | 138.5 | 133.9 | 3.46 | 3.378 | 13.13 | 12.82 |  | 3378
June | 97.5 | 16.1 | 121.3 | 116.8 | 3.073 | 3.002 | 13.31 | 13 |  | 3002
July | 111.9 | 15.4 | 139.3 | 134.5 | 3.538 | 3.456 | 13.34 | 13.03 |  | 3456
August | 139.5 | 16.2 | 164.2 | 159.2 | 4.1 | 4.001 | 13.11 | 12.8 |  | 4001
September | 165.8 | 19 | 181.3 | 176 | 4.434 | 4.324 | 12.85 | 12.53 |  | 4324
October | 186.9 | 21.1 | 191.4 | 185.5 | 4.622 | 4.506 | 12.69 | 12.37 |  | 4506
November | 195.8 | 22.2 | 191.5 | 185.5 | 4.581 | 4.468 | 12.57 | 12.26 |  | 4468
December | 239.4 | 24.1 | 227.5 | 220.8 | 5.323 | 5.188 | 12.29 | 11.98 |  | 5188
|  | January | February | March | April | May | June | July | August | September | October | November | December | Total
Wamuran | Chris | 4681.248 | 3763.0507 | 4040.9327 | 3211.5398 | 2720.808 | 2316.58 | 2694.1067 | 3281.5773 | 3979.4998 | 4335.3293 | 4523.92 | 4897.5247 | 44446.117
| Andrew | 4494.3576 | 3612.8176 | 3879.6057 | 3083.3249 | 2612.1846 | 2224.0947 | 2586.5493 | 3150.5663 | 3820.6254 | 4162.2491 | 4343.3106 | 4701.9998 | 42671.6858
| PVsyst outputs | 4401 | 3719 | 4044 | 3690 | 3378 | 3002 | 3456 | 4001 | 4324 | 4506 | 4468 | 5188 | 48177 |  | Temperature effects | 1.129 | 12% more energy than Andrew's estimate….
Moorooduc
Note on A8: Chris Davies: Assume 30 kW system, 80% system efficiency